Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | TO->FROM | 655048 LAKECNTY-ER8 69.0 655119 LAKECNTY-ER7 115 1 | 56 | 56 | 0.29305 | 118.51 | 655462 ARLNGTN-ER7 115 655554 KNGSBURY-ER7 115 1 | Cumulative Impact | Multi - Madison, SD Area 115 kV System Voltage Conversion
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | TO->FROM | 655048 LAKECNTY-ER8 69.0 655119 LAKECNTY-ER7 115 1 | 56 | 56 | 0.11672 | 113.03 | P12:115:UMZW:# 125 #:: AUR IN SD. AUR-FL BRANCH FAULT:HV: | Cumulative Impact | Multi - Madison, SD Area 115 kV System Voltage Conversion
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 655048 LAKECNTY-ER8 69.0 655223 WENTWRTH-ER8 69.0 1 | 35 | 35 | 0.29269 | 130.76 | P12:115:UMZW:# 1521 #:: AG IN SD. AG-BR BRANCH FAULT (AG IS A TAP):HV: | Cumulative Impact | Multi - Madison, SD Area 115 kV System Voltage Conversion
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 655048 LAKECNTY-ER8 69.0 655223 WENTWRTH-ER8 69.0 1 | 35 | 35 | 0.29269 | 130.71 | P12:115:UMZ:# 20008 #:: PROPER N-1 FOR TAP ARLNGTN-ER7:HV: | Cumulative Impact | Multi - Madison, SD Area 115 kV System Voltage Conversion
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 655048 LAKECNTY-ER8 69.0 655223 WENTWRTH-ER8 69.0 1 | 35 | 35 | 0.29305 | 129.27 | 655462 ARLNGTN-ER7 115 655554 KNGSBURY-ER7 115 1 | Cumulative Impact | Multi - Madison, SD Area 115 kV System Voltage Conversion
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 655048 LAKECNTY-ER8 69.0 655223 WENTWRTH-ER8 69.0 1 | 35 | 35 | 0.11672 | 128.76 | P12:115:UMZW:# 124 #:: AUR IN SD. AUR-BR BRANCH FAULT:HV: | Cumulative Impact | Multi - Madison, SD Area 115 kV System Voltage Conversion
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 655048 LAKECNTY-ER8 69.0 655223 WENTWRTH-ER8 69.0 1 | 35 | 35 | 0.11672 | 120.22 | P12:115:UMZW:# 125 #:: AUR IN SD. AUR-FL BRANCH FAULT:HV: | Cumulative Impact | Multi - Madison, SD Area 115 kV System Voltage Conversion
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.06143 | 120.05 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.05964 | 120.05 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.09666 | 120.05 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.08653 | 120.05 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.05925 | 120.05 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.06143 | 120.04 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.05964 | 120.04 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.09666 | 120.04 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.08653 | 120.04 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.05925 | 120.04 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.06212 | 120.1 | POI 652532_2 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.06021 | 120.1 | POI 652532_2 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.0973 | 120.1 | POI 652532_2 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.08718 | 120.1 | POI 652532_2 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.05987 | 120.1 | POI 652532_2 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.06106 | 120.34 | POI 652532_1 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.06033 | 120.34 | POI 652532_1 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.09612 | 120.34 | POI 652532_1 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.08603 | 120.34 | POI 652532_1 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.05862 | 120.34 | POI 652532_1 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.0612 | 119.49 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.06046 | 119.49 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.09625 | 119.49 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.08616 | 119.49 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.05875 | 119.49 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.06189 | 119.37 | POI 652532_2 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.06103 | 119.37 | POI 652532_2 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.09689 | 119.37 | POI 652532_2 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.08681 | 119.37 | POI 652532_2 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.05936 | 119.37 | POI 652532_2 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.0612 | 119.37 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.06046 | 119.37 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.09625 | 119.37 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.08616 | 119.37 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.05875 | 119.37 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.0612 | 119.3 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.06046 | 119.3 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.09625 | 119.3 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.08616 | 119.3 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.05875 | 119.3 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-012 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.05995 | 107.37 | POI 652532_1 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-097 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.06173 | 107.37 | POI 652532_1 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-105 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.09503 | 107.37 | POI 652532_1 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-154 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.08491 | 107.37 | POI 652532_1 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-182 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.05817 | 107.37 | POI 652532_1 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-012 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.06086 | 105.88 | POI 652532_2 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-097 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.06252 | 105.88 | POI 652532_2 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-105 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.09589 | 105.88 | POI 652532_2 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-154 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.08578 | 105.88 | POI 652532_2 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-182 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.059 | 105.88 | POI 652532_2 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-012 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.06021 | 105.72 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-097 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.06199 | 105.72 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-105 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.09528 | 105.72 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-154 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.08517 | 105.72 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-182 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.05843 | 105.72 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-012 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.06021 | 105.63 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-097 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.06199 | 105.63 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-105 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.09528 | 105.63 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-154 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.08517 | 105.63 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-182 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.05843 | 105.63 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-012 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.06021 | 105.63 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-097 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.06199 | 105.63 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-105 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.09528 | 105.63 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-154 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.08517 | 105.63 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-182 | TO->FROM | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 320 | 320 | 0.05843 | 105.63 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-182 | FROM->TO | 652499 CAMPBELL 4 230 661038 GLENHAM4 230 1 | 240 | 264 | 0.03171 | 101.32 | System Intact | TDF Impact | Rebuild the CAMPBELL 4 to GLENHAM4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 652806 FTTHOM1-LNX3 345 Z | 760 | 760 | 0.84183 | 120.47 | 652506 FTTHOMP3 345 659130 CHAPELLE-BE3 345 2 | Cumulative Impact | FTTHOMP3 to FTTHOM1-LNX3 345 kV Line Z Rating Update
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-182 | TO->FROM | 652506 FTTHOMP3 345 652806 FTTHOM1-LNX3 345 Z | 760 | 760 | 0.10688 | 120.47 | 652506 FTTHOMP3 345 659130 CHAPELLE-BE3 345 2 | Cumulative Impact | FTTHOMP3 to FTTHOM1-LNX3 345 kV Line Z Rating Update
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652506 FTTHOMP3 345 652806 FTTHOM1-LNX3 345 Z | 760 | 760 | 0.13653 | 112.23 | 652506 FTTHOMP3 345 659130 CHAPELLE-BE3 345 2 | Cumulative Impact | FTTHOMP3 to FTTHOM1-LNX3 345 kV Line Z Rating Update
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 652806 FTTHOM1-LNX3 345 Z | 760 | 760 | 0.84715 | 112.23 | 652506 FTTHOMP3 345 659130 CHAPELLE-BE3 345 2 | Cumulative Impact | FTTHOMP3 to FTTHOM1-LNX3 345 kV Line Z Rating Update
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | TO->FROM | 652506 FTTHOMP3 345 652806 FTTHOM1-LNX3 345 Z | 760 | 760 | 0.11353 | 112.23 | 652506 FTTHOMP3 345 659130 CHAPELLE-BE3 345 2 | Cumulative Impact | FTTHOMP3 to FTTHOM1-LNX3 345 kV Line Z Rating Update
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652506 FTTHOMP3 345 652806 FTTHOM1-LNX3 345 Z | 760 | 760 | 0.14558 | 107.72 | 652506 FTTHOMP3 345 659130 CHAPELLE-BE3 345 2 | Cumulative Impact | FTTHOMP3 to FTTHOM1-LNX3 345 kV Line Z Rating Update
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 652806 FTTHOM1-LNX3 345 Z | 760 | 760 | 0.84578 | 107.72 | 652506 FTTHOMP3 345 659130 CHAPELLE-BE3 345 2 | Cumulative Impact | FTTHOMP3 to FTTHOM1-LNX3 345 kV Line Z Rating Update
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 652506 FTTHOMP3 345 652806 FTTHOM1-LNX3 345 Z | 760 | 760 | 0.11082 | 107.72 | 652506 FTTHOMP3 345 659130 CHAPELLE-BE3 345 2 | Cumulative Impact | FTTHOMP3 to FTTHOM1-LNX3 345 kV Line Z Rating Update
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 659311 PAHOJA__-BE4 230 659900 EAGLE___-NI4 230 1 | 373 | 373 | 0.11993 | 102.86 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the PAHOJA__-BE4 to EAGLE___-NI4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 659311 PAHOJA__-BE4 230 659900 EAGLE___-NI4 230 1 | 373 | 373 | 0.09982 | 102.86 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the PAHOJA__-BE4 to EAGLE___-NI4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 659311 PAHOJA__-BE4 230 659900 EAGLE___-NI4 230 1 | 373 | 373 | 0.0596 | 102.86 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the PAHOJA__-BE4 to EAGLE___-NI4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 659311 PAHOJA__-BE4 230 659900 EAGLE___-NI4 230 1 | 373 | 373 | 0.06217 | 102.86 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the PAHOJA__-BE4 to EAGLE___-NI4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 659311 PAHOJA__-BE4 230 659900 EAGLE___-NI4 230 1 | 373 | 373 | 0.07496 | 102.86 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the PAHOJA__-BE4 to EAGLE___-NI4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 659311 PAHOJA__-BE4 230 659900 EAGLE___-NI4 230 1 | 373 | 373 | 0.07076 | 102.86 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the PAHOJA__-BE4 to EAGLE___-NI4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 659311 PAHOJA__-BE4 230 659900 EAGLE___-NI4 230 1 | 373 | 373 | 0.1192 | 100.64 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the PAHOJA__-BE4 to EAGLE___-NI4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 659311 PAHOJA__-BE4 230 659900 EAGLE___-NI4 230 1 | 373 | 373 | 0.09905 | 100.64 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the PAHOJA__-BE4 to EAGLE___-NI4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 659311 PAHOJA__-BE4 230 659900 EAGLE___-NI4 230 1 | 373 | 373 | 0.06013 | 100.64 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the PAHOJA__-BE4 to EAGLE___-NI4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 659311 PAHOJA__-BE4 230 659900 EAGLE___-NI4 230 1 | 373 | 373 | 0.06176 | 100.64 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the PAHOJA__-BE4 to EAGLE___-NI4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 659311 PAHOJA__-BE4 230 659900 EAGLE___-NI4 230 1 | 373 | 373 | 0.07453 | 100.64 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the PAHOJA__-BE4 to EAGLE___-NI4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 659311 PAHOJA__-BE4 230 659900 EAGLE___-NI4 230 1 | 373 | 373 | 0.07008 | 100.64 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the PAHOJA__-BE4 to EAGLE___-NI4 230kV Line 1
Non-Converged | DISIS-2023-001 | 01ALL | 0 | 27L | GEN-2023-012 |  | Non-Converged |  |  | 0.10038 |  | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | TDF Impact | Build new GR PRAIRIE 3 to ANTELOPE 3 345kV Line 1
Non-Converged | DISIS-2023-001 | 01ALL | 0 | 27L | GEN-2023-105 |  | Non-Converged |  |  | 0.23985 |  | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | TDF Impact | Build new GR PRAIRIE 3 to ANTELOPE 3 345kV Line 1
Non-Converged | DISIS-2023-001 | 01ALL | 0 | 27L | GEN-2023-182 |  | Non-Converged |  |  | 0.1089 |  | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | TDF Impact | Build new GR PRAIRIE 3 to ANTELOPE 3 345kV Line 1
Non-Converged | DISIS-2023-001 | 01ALL | 0 | 27L | GEN-2023-012 |  | Non-Converged |  |  | 0.10038 |  | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | TDF Impact | Build new GR PRAIRIE 3 to ANTELOPE 3 345kV Line 1
Non-Converged | DISIS-2023-001 | 01ALL | 0 | 27L | GEN-2023-105 |  | Non-Converged |  |  | 0.23985 |  | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | TDF Impact | Build new GR PRAIRIE 3 to ANTELOPE 3 345kV Line 1
Non-Converged | DISIS-2023-001 | 01ALL | 0 | 27L | GEN-2023-182 |  | Non-Converged |  |  | 0.1089 |  | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | TDF Impact | Build new GR PRAIRIE 3 to ANTELOPE 3 345kV Line 1
Non-Converged | DISIS-2023-001 | 01ALL | 0 | 24SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2023-001 | 01ALL | 0 | 27SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2023-001 | 01ALL | 0 | 27WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2023-001 | 01NR | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2023-001 | 01NR | 1 | 27L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 996590 FT2 KU1A 230 1 | 250 | 313 | 0.40926 | 129.29 | POI 652532_1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 996590 FT2 KU1A 230 1 | 250 | 313 | 0.40948 | 128.72 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 996590 FT2 KU1A 230 1 | 250 | 313 | 0.4094 | 128.57 | POI 652532_2 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 996590 FT2 KU1A 230 1 | 250 | 313 | 0.40926 | 127.67 | POI 652532_1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 996590 FT2 KU1A 230 1 | 250 | 313 | 0.40948 | 127.18 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 996590 FT2 KU1A 230 1 | 250 | 313 | 0.4094 | 127.06 | POI 652532_2 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 996589 FT2 KU1B 230 1 | 250 | 313 | 0.40059 | 126.55 | POI 652532_1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 996590 FT2 KU1A 230 1 | 250 | 313 | 0.40948 | 126.63 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 996590 FT2 KU1A 230 1 | 250 | 313 | 0.40948 | 126.11 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 996590 FT2 KU1A 230 1 | 250 | 313 | 0.40948 | 126.56 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 996589 FT2 KU1B 230 1 | 250 | 313 | 0.40082 | 126 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 996590 FT2 KU1A 230 1 | 250 | 313 | 0.40948 | 126.02 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 996589 FT2 KU1B 230 1 | 250 | 313 | 0.40073 | 125.85 | POI 652532_2 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 996589 FT2 KU1B 230 1 | 250 | 313 | 0.40059 | 124.96 | POI 652532_1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 996589 FT2 KU1B 230 1 | 250 | 313 | 0.40082 | 124.49 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 996589 FT2 KU1B 230 1 | 250 | 313 | 0.40073 | 124.37 | POI 652532_2 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 996589 FT2 KU1B 230 1 | 250 | 313 | 0.40082 | 123.95 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 996589 FT2 KU1B 230 1 | 250 | 313 | 0.40082 | 123.44 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 996589 FT2 KU1B 230 1 | 250 | 313 | 0.40082 | 123.88 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 996589 FT2 KU1B 230 1 | 250 | 313 | 0.40082 | 123.35 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652506 FTTHOMP3 345 996593 FT2 KU1A 230 1 | 250 | 313 | 0.06096 | 117.68 | POI 652532_1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 996593 FT2 KU1A 230 1 | 250 | 313 | 0.41132 | 117.68 | POI 652532_1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652506 FTTHOMP3 345 996593 FT2 KU1A 230 1 | 250 | 313 | 0.06101 | 117.41 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 996593 FT2 KU1A 230 1 | 250 | 313 | 0.41137 | 117.41 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652506 FTTHOMP3 345 996593 FT2 KU1A 230 1 | 250 | 313 | 0.06092 | 117.35 | POI 652532_2 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 996593 FT2 KU1A 230 1 | 250 | 313 | 0.41126 | 117.35 | POI 652532_2 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 996593 FT2 KU1A 230 1 | 250 | 313 | 0.06096 | 116.09 | POI 652532_1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 996593 FT2 KU1A 230 1 | 250 | 313 | 0.41132 | 116.09 | POI 652532_1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 996593 FT2 KU1A 230 1 | 250 | 313 | 0.06101 | 115.9 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 996593 FT2 KU1A 230 1 | 250 | 313 | 0.41137 | 115.9 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 996593 FT2 KU1A 230 1 | 250 | 313 | 0.06092 | 115.86 | POI 652532_2 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 996593 FT2 KU1A 230 1 | 250 | 313 | 0.41126 | 115.86 | POI 652532_2 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652506 FTTHOMP3 345 996593 FT2 KU1A 230 1 | 250 | 313 | 0.06101 | 115.32 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 996593 FT2 KU1A 230 1 | 250 | 313 | 0.41137 | 115.32 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652506 FTTHOMP3 345 996593 FT2 KU1A 230 1 | 250 | 313 | 0.06101 | 115.32 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 996593 FT2 KU1A 230 1 | 250 | 313 | 0.41137 | 115.32 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652506 FTTHOMP3 345 996592 FT2 KU1B 230 1 | 250 | 313 | 0.05967 | 115.19 | POI 652532_1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 996592 FT2 KU1B 230 1 | 250 | 313 | 0.40262 | 115.19 | POI 652532_1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652506 FTTHOMP3 345 996592 FT2 KU1B 230 1 | 250 | 313 | 0.05972 | 114.92 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 996592 FT2 KU1B 230 1 | 250 | 313 | 0.40266 | 114.92 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652506 FTTHOMP3 345 996592 FT2 KU1B 230 1 | 250 | 313 | 0.05963 | 114.87 | POI 652532_2 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 996592 FT2 KU1B 230 1 | 250 | 313 | 0.40256 | 114.87 | POI 652532_2 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 996593 FT2 KU1A 230 1 | 250 | 313 | 0.06101 | 114.69 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 996593 FT2 KU1A 230 1 | 250 | 313 | 0.41137 | 114.69 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 996593 FT2 KU1A 230 1 | 250 | 313 | 0.06101 | 114.69 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 996593 FT2 KU1A 230 1 | 250 | 313 | 0.41137 | 114.69 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 996592 FT2 KU1B 230 1 | 250 | 313 | 0.05967 | 113.63 | POI 652532_1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 996592 FT2 KU1B 230 1 | 250 | 313 | 0.40262 | 113.63 | POI 652532_1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 996592 FT2 KU1B 230 1 | 250 | 313 | 0.05972 | 113.45 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 996592 FT2 KU1B 230 1 | 250 | 313 | 0.40266 | 113.45 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 996592 FT2 KU1B 230 1 | 250 | 313 | 0.05963 | 113.41 | POI 652532_2 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 996592 FT2 KU1B 230 1 | 250 | 313 | 0.40256 | 113.41 | POI 652532_2 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652506 FTTHOMP3 345 996592 FT2 KU1B 230 1 | 250 | 313 | 0.05972 | 112.88 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 996592 FT2 KU1B 230 1 | 250 | 313 | 0.40266 | 112.88 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652506 FTTHOMP3 345 996592 FT2 KU1B 230 1 | 250 | 313 | 0.05972 | 112.87 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 996592 FT2 KU1B 230 1 | 250 | 313 | 0.40266 | 112.87 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 996592 FT2 KU1B 230 1 | 250 | 313 | 0.05972 | 112.26 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 996592 FT2 KU1B 230 1 | 250 | 313 | 0.40266 | 112.26 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 996592 FT2 KU1B 230 1 | 250 | 313 | 0.05972 | 112.26 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 996592 FT2 KU1B 230 1 | 250 | 313 | 0.40266 | 112.26 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652506 FTTHOMP3 345 996590 FT2 KU1A 230 1 | 250 | 313 | 0.06197 | 113.75 | POI 652532_1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 996590 FT2 KU1A 230 1 | 250 | 313 | 0.41108 | 113.75 | POI 652532_1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652506 FTTHOMP3 345 996590 FT2 KU1A 230 1 | 250 | 313 | 0.06201 | 113.46 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 996590 FT2 KU1A 230 1 | 250 | 313 | 0.41112 | 113.46 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652506 FTTHOMP3 345 996590 FT2 KU1A 230 1 | 250 | 313 | 0.06192 | 113.41 | POI 652532_2 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 996590 FT2 KU1A 230 1 | 250 | 313 | 0.41101 | 113.41 | POI 652532_2 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 996590 FT2 KU1A 230 1 | 250 | 313 | 0.06197 | 112.16 | POI 652532_1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 996590 FT2 KU1A 230 1 | 250 | 313 | 0.41108 | 112.16 | POI 652532_1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 996590 FT2 KU1A 230 1 | 250 | 313 | 0.06201 | 111.91 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 996590 FT2 KU1A 230 1 | 250 | 313 | 0.41112 | 111.91 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 996590 FT2 KU1A 230 1 | 250 | 313 | 0.06192 | 111.87 | POI 652532_2 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 996590 FT2 KU1A 230 1 | 250 | 313 | 0.41101 | 111.87 | POI 652532_2 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652506 FTTHOMP3 345 996590 FT2 KU1A 230 1 | 250 | 313 | 0.06201 | 111.42 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 996590 FT2 KU1A 230 1 | 250 | 313 | 0.41112 | 111.42 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652506 FTTHOMP3 345 996590 FT2 KU1A 230 1 | 250 | 313 | 0.06201 | 111.42 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 996590 FT2 KU1A 230 1 | 250 | 313 | 0.41112 | 111.42 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652506 FTTHOMP3 345 996589 FT2 KU1B 230 1 | 250 | 313 | 0.06065 | 111.34 | POI 652532_1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 996589 FT2 KU1B 230 1 | 250 | 313 | 0.40238 | 111.34 | POI 652532_1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652506 FTTHOMP3 345 996589 FT2 KU1B 230 1 | 250 | 313 | 0.0607 | 111.06 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 996589 FT2 KU1B 230 1 | 250 | 313 | 0.40242 | 111.06 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652506 FTTHOMP3 345 996589 FT2 KU1B 230 1 | 250 | 313 | 0.06061 | 111 | POI 652532_2 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 996589 FT2 KU1B 230 1 | 250 | 313 | 0.40231 | 111 | POI 652532_2 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 996590 FT2 KU1A 230 1 | 250 | 313 | 0.06201 | 110.84 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 996590 FT2 KU1A 230 1 | 250 | 313 | 0.41112 | 110.84 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 996590 FT2 KU1A 230 1 | 250 | 313 | 0.06201 | 110.84 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 996590 FT2 KU1A 230 1 | 250 | 313 | 0.41112 | 110.84 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 996589 FT2 KU1B 230 1 | 250 | 313 | 0.06065 | 109.79 | POI 652532_1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 996589 FT2 KU1B 230 1 | 250 | 313 | 0.40238 | 109.79 | POI 652532_1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 996589 FT2 KU1B 230 1 | 250 | 313 | 0.0607 | 109.54 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 996589 FT2 KU1B 230 1 | 250 | 313 | 0.40242 | 109.54 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 996589 FT2 KU1B 230 1 | 250 | 313 | 0.06061 | 109.5 | POI 652532_2 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 996589 FT2 KU1B 230 1 | 250 | 313 | 0.40231 | 109.5 | POI 652532_2 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652506 FTTHOMP3 345 996589 FT2 KU1B 230 1 | 250 | 313 | 0.0607 | 109.06 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 996589 FT2 KU1B 230 1 | 250 | 313 | 0.40242 | 109.06 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652506 FTTHOMP3 345 996589 FT2 KU1B 230 1 | 250 | 313 | 0.0607 | 109.06 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 996589 FT2 KU1B 230 1 | 250 | 313 | 0.40242 | 109.06 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 996589 FT2 KU1B 230 1 | 250 | 313 | 0.0607 | 108.49 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 996589 FT2 KU1B 230 1 | 250 | 313 | 0.40242 | 108.49 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 996589 FT2 KU1B 230 1 | 250 | 313 | 0.0607 | 108.49 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 996589 FT2 KU1B 230 1 | 250 | 313 | 0.40242 | 108.49 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build Third Ft Thompson 345-230 kV Transformer
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.10199 | 106.71 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08292 | 106.71 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.11571 | 106.71 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.2385 | 106.71 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.15448 | 106.71 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.11282 | 106.71 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-012 | TO->FROM | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 717 | 717 | 0.10199 | 105.45 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-082 | TO->FROM | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 717 | 717 | 0.08292 | 105.45 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 717 | 717 | 0.11571 | 105.45 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 717 | 717 | 0.2385 | 105.45 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-154 | TO->FROM | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 717 | 717 | 0.15448 | 105.45 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 24SP | GEN-2023-182 | TO->FROM | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 717 | 717 | 0.11282 | 105.45 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.22083 | 118.65 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 717 | 717 | 0.22083 | 117.49 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | TDF Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.10166 | 105.08 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.08259 | 105.08 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.1164 | 105.08 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.23821 | 105.08 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.15415 | 105.08 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.11244 | 105.08 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-012 | TO->FROM | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 717 | 717 | 0.10166 | 103.94 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-082 | TO->FROM | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 717 | 717 | 0.08259 | 103.94 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 717 | 717 | 0.1164 | 103.94 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 717 | 717 | 0.23821 | 103.94 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-154 | TO->FROM | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 717 | 717 | 0.15415 | 103.94 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 717 | 717 | 0.11244 | 103.94 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27WP | GEN-2023-012 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.09598 | 102.97 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27WP | GEN-2023-082 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.07676 | 102.97 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27WP | GEN-2023-097 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.11745 | 102.97 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27WP | GEN-2023-105 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.23207 | 102.97 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27WP | GEN-2023-154 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.14859 | 102.97 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27WP | GEN-2023-182 | FROM->TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.10839 | 102.97 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27WP | GEN-2023-012 | TO->FROM | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 717 | 717 | 0.09598 | 102.31 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27WP | GEN-2023-082 | TO->FROM | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 717 | 717 | 0.07676 | 102.31 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27WP | GEN-2023-097 | TO->FROM | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 717 | 717 | 0.11745 | 102.31 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27WP | GEN-2023-105 | TO->FROM | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 717 | 717 | 0.23207 | 102.31 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27WP | GEN-2023-154 | TO->FROM | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 717 | 717 | 0.14859 | 102.31 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Thermal | DISIS-2023-001 CF | 01ALL | 1 | 27WP | GEN-2023-182 | TO->FROM | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 717 | 717 | 0.10839 | 102.31 | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
Non-Converged | DISIS-2023-001 CF | 01ALL | 0 | 24SP | GEN-2023-097 |  | Non-Converged |  |  | 0.13746 |  | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | TDF Impact | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
Non-Converged | DISIS-2023-001 CF | 01ALL | 0 | 24SP | GEN-2023-105 |  | Non-Converged |  |  | 0.83665 |  | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | TDF Impact | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
Non-Converged | DISIS-2023-001 CF | 01ALL | 0 | 24SP | GEN-2023-182 |  | Non-Converged |  |  | 0.11322 |  | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | TDF Impact | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
Non-Converged | DISIS-2023-001 CF | 01ALL | 0 | 24SP | GEN-2023-097 |  | Non-Converged |  |  | 0.13746 |  | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV: | TDF Impact | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
Non-Converged | DISIS-2023-001 CF | 01ALL | 0 | 24SP | GEN-2023-105 |  | Non-Converged |  |  | 0.83665 |  | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV: | TDF Impact | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
Non-Converged | DISIS-2023-001 CF | 01ALL | 0 | 24SP | GEN-2023-182 |  | Non-Converged |  |  | 0.11322 |  | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV: | TDF Impact | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
Non-Converged | DISIS-2023-001 CF | 01ALL | 0 | 24SP | GEN-2023-097 |  | Non-Converged |  |  | 0.13746 |  | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1 | TDF Impact | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
Non-Converged | DISIS-2023-001 CF | 01ALL | 0 | 24SP | GEN-2023-105 |  | Non-Converged |  |  | 0.83665 |  | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1 | TDF Impact | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
Non-Converged | DISIS-2023-001 CF | 01ALL | 0 | 24SP | GEN-2023-182 |  | Non-Converged |  |  | 0.11322 |  | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1 | TDF Impact | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
Non-Converged | DISIS-2023-001 CF | 01ALL | 0 | 27L | GEN-2023-105 |  | Non-Converged |  |  | 0.83245 |  | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | TDF Impact | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
Non-Converged | DISIS-2023-001 CF | 01ALL | 0 | 27L | GEN-2023-182 |  | Non-Converged |  |  | 0.10892 |  | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | TDF Impact | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
Non-Converged | DISIS-2023-001 CF | 01ALL | 0 | 27L | GEN-2023-105 |  | Non-Converged |  |  | 0.83245 |  | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV: | TDF Impact | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
Non-Converged | DISIS-2023-001 CF | 01ALL | 0 | 27L | GEN-2023-182 |  | Non-Converged |  |  | 0.10892 |  | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV: | TDF Impact | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
Non-Converged | DISIS-2023-001 CF | 01ALL | 0 | 27L | GEN-2023-105 |  | Non-Converged |  |  | 0.83245 |  | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1 | TDF Impact | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
Non-Converged | DISIS-2023-001 CF | 01ALL | 0 | 27L | GEN-2023-182 |  | Non-Converged |  |  | 0.10892 |  | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1 | TDF Impact | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
Non-Converged | DISIS-2023-001 CF | 01ALL | 0 | 27SP | GEN-2023-097 |  | Non-Converged |  |  | 0.13952 |  | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | TDF Impact | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
Non-Converged | DISIS-2023-001 CF | 01ALL | 0 | 27SP | GEN-2023-105 |  | Non-Converged |  |  | 0.83612 |  | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | TDF Impact | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
Non-Converged | DISIS-2023-001 CF | 01ALL | 0 | 27SP | GEN-2023-182 |  | Non-Converged |  |  | 0.11259 |  | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | TDF Impact | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
Non-Converged | DISIS-2023-001 CF | 01ALL | 0 | 27SP | GEN-2023-097 |  | Non-Converged |  |  | 0.13952 |  | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV: | TDF Impact | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
Non-Converged | DISIS-2023-001 CF | 01ALL | 0 | 27SP | GEN-2023-105 |  | Non-Converged |  |  | 0.83612 |  | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV: | TDF Impact | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
Non-Converged | DISIS-2023-001 CF | 01ALL | 0 | 27SP | GEN-2023-182 |  | Non-Converged |  |  | 0.11259 |  | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV: | TDF Impact | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
Non-Converged | DISIS-2023-001 CF | 01ALL | 0 | 27SP | GEN-2023-097 |  | Non-Converged |  |  | 0.13952 |  | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1 | TDF Impact | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
Non-Converged | DISIS-2023-001 CF | 01ALL | 0 | 27SP | GEN-2023-105 |  | Non-Converged |  |  | 0.83612 |  | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1 | TDF Impact | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
Non-Converged | DISIS-2023-001 CF | 01ALL | 0 | 27SP | GEN-2023-182 |  | Non-Converged |  |  | 0.11259 |  | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1 | TDF Impact | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
Non-Converged | DISIS-2023-001 CF | 01ALL | 0 | 27WP | GEN-2023-097 |  | Non-Converged |  |  | 0.15178 |  | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | TDF Impact | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
Non-Converged | DISIS-2023-001 CF | 01ALL | 0 | 27WP | GEN-2023-105 |  | Non-Converged |  |  | 0.83604 |  | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | TDF Impact | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
Non-Converged | DISIS-2023-001 CF | 01ALL | 0 | 27WP | GEN-2023-182 |  | Non-Converged |  |  | 0.11476 |  | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | TDF Impact | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
Non-Converged | DISIS-2023-001 CF | 01ALL | 0 | 27WP | GEN-2023-097 |  | Non-Converged |  |  | 0.15178 |  | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV: | TDF Impact | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
Non-Converged | DISIS-2023-001 CF | 01ALL | 0 | 27WP | GEN-2023-105 |  | Non-Converged |  |  | 0.83604 |  | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV: | TDF Impact | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
Non-Converged | DISIS-2023-001 CF | 01ALL | 0 | 27WP | GEN-2023-182 |  | Non-Converged |  |  | 0.11476 |  | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV: | TDF Impact | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
Non-Converged | DISIS-2023-001 CF | 01ALL | 0 | 27WP | GEN-2023-097 |  | Non-Converged |  |  | 0.15178 |  | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1 | TDF Impact | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
Non-Converged | DISIS-2023-001 CF | 01ALL | 0 | 27WP | GEN-2023-105 |  | Non-Converged |  |  | 0.83604 |  | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1 | TDF Impact | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
Non-Converged | DISIS-2023-001 CF | 01ALL | 0 | 27WP | GEN-2023-182 |  | Non-Converged |  |  | 0.11476 |  | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1 | TDF Impact | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.07 | System-Intact | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.07 | System-Intact | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.07 | System-Intact | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 141.71 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.07 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.63 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 174.4 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.51 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 170.93 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 141.71 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.07 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.63 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 174.4 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.51 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 170.93 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.44 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.09 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.63 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 174.4 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.59 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 170.93 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.44 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.09 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.63 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 174.4 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.59 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 170.93 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.12 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.34 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.52 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.73 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.32 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 170.96 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.12 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.34 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.52 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.73 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.32 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 170.96 | System-Intact | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.54961 | 105.32 | P42:345:OPPD-LES:S3454-S3455&WAG:::EHV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.57209 | 113.2 | P42:345:MEC-OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.57209 | 113.2 | P45:345:OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.59009 | 111.84 | P12:345:OPPD:LX007::S3458.S3456.CKT1:: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.59407 | 106.09 | 635200 RAUN 3 345 762779 G18-043 TAP 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.59407 | 107.18 | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.59407 | 107.18 | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.59571 | 104.59 | P21:345:MEC-OPPD:AUTO-SINGLE:CBLUFFS3:S34563:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.6032 | 109.01 | P23:345:MEC:CBEC 905 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 106.69 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 106.69 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 106.83 | P23:345:MEC:ATCHISON CO 903 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 107.07 | 635017 ATCHISON 3 345 635018 WESTBORO 3 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 107.34 | Potential P4 Event - POI 635018_0 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 107.34 | Potential P4 Event - POI 635018_1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 107.34 | Potential P4 Event - POI 635018_2 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 107.74 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60424 | 105.07 | P23:345:AMMO::MAYWOOD:V33:: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60432 | 104.34 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60432 | 104.68 | P23:345:AMMO:::24SPENCERCREEK:EHV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60446 | 104.24 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60475 | 104.37 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60488 | 104.34 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.6049 | 108.85 | P23:345:MEC:CBEC 908 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60492 | 104.23 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60492 | 104.38 | P12:345:WERE:N345-AECI-345:::EHV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60493 | 104.25 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60495 | 104.29 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60495 | 104.29 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60495 | 104.3 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60496 | 104.39 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60496 | 104.39 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60496 | 104.39 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60497 | 104.14 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60497 | 104.19 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60497 | 104.26 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.15 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.17 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.18 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.19 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.42 | P12:500:EES-EAI:DRIVER:SHELBY | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.42 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.49 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.49 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.03 | 515853 DGRASSE4 138 763769 GEN-2019-045 138 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.11 | 520826 BENNGTN4 138 521115 BENNSUB4 138 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.11 | P12:HV:EES::3VIENNA_LA!:3RUSTON:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.11 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.12 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.12 | 514722 CLEVETP2 69.0 514723 CLEVLND2 69.0 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.14 | 515149 MADINDT4 138 515158 MADLIND4 138 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 346093 2LATHROP 69.0 344923 5LATHROP 161 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 523143 NP-PERDUR_G3 115 523186 SPEARMAN 3 115 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 523186 SPEARMAN 3 115 3WXFMR VON 13770/1 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 525731 SP-ABNTYPOI2 69.0 525816 TUCO_INT2 2 69.0 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.16 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.17 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.19 | 509829 FULTONW4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.22 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.23 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.25 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.26 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.26 | P12:161:OKGE:BKRBKR197:::: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.3 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.33 | 635580 ARBOR HILL 3 345 635582 ARBR HL B2 9 34.5 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.33 | P12:HV:EES::6DRIVER%:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.37 | 646211 S1211 5 161 645023 N OMA 3G 13.8 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.39 | P12:115:WERE:EMAN-KSU-115:::HV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.39 | P13:138-115:MP:TCH:TR4(1) | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.42 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.42 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.44 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.48 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.5 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.56 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.57 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.57 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.59 | P13:NBEC#1 GSU | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.63 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.68 | P13:SH902T GSU | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.69 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.7 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.72 | 762712 G18-037-TAP 161 762713 GEN-2018-037 161 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.72 | P11:18:SPC: BD #6+SSL:::HV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.77 | P11:18:SPC: BD #6:::HV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.79 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.8 | P11:024:DPC:ALMA2:6 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.91 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.99 | 764601 G20-025-GEN1 20.0 764600 GEN-2020-025 161 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.99 | 775961 GEN-2023-199 230 775962 G23-199XFMR1 34.5 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.99 | GEN-2020-028_POI_646363_Generator_outage | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.99 | GEN-2023-199_POI_640386_Generator_outage | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.04 | 762779 G18-043 TAP 345 762780 GEN-2018-043 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.08 | 764661 G20-031-GEN1 20.0 764660 GEN-2020-031 161 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.08 | GEN-2020-031_POI_646363_Generator_outage | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.24 | P11:115:XEL:HBR #6 7 8 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.25 | P11:20:XEL:AUTO-SINGLE:KING31G:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.28 | P23:345:XEL:8H14 PRI | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.3 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.3 | P23:345:XEL:8H17 PRI AS | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.35 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.48 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.49 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.5 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.54 | P23:345:XEL:8N8 MNN | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.58 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.58 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.9 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 106.01 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 106.23 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 106.83 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 106.98 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 108.9 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 109.21 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 109.42 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 110.09 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.605 | 104.19 | 344536 7ENON_TP 345 345217 7ROOTBEER 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.605 | 104.2 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60504 | 104.34 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60506 | 104.17 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60509 | 104.21 | 532791 BENTON 7 345 766141 G21-096-TAP 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60511 | 104.13 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60511 | 104.28 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60555 | 104.6 | 767240 G22-013-TAP 345 776600 G23-231-TAP 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60555 | 104.95 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60566 | 104.26 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.6057 | 105.04 | 300076 5FAIRPTB2 161 301559 5FAIRPTXF3 161 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.6057 | 105.04 | 301559 5FAIRPTXF3 161 300039 7FAIRPT 345 3 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60601 | 104.24 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60648 | 104.75 | 300039 7FAIRPT 345 640139 COOPER 3 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.6074 | 108.19 | P42:345:NPPD:BKR-CPR-3304:::: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.57 | Potential P4 Event - POI 541510_3 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.78 | Potential P4 Event - POI 541510_1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.8 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.82 | 541197 MULLNCR7 345 541510 HOLT 7 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.82 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.82 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.87 | 541197 MULLNCR7 345 771140 G22-208-TAP 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61786 | 106.38 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61786 | 106.39 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61786 | 106.45 | Potential P4 Event - POI 541510_0 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 119.18 | Potential P4 Event - POI 645740_10 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 134.5 | Potential P4 Event - POI 645740_11 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.54 | P12:345:OPPD:LX008::S3458.S3740.CKT1:: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.54 | P22:345:OPPD:S3458-S3740:::EHV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.54 | P22:345:OPPD:S3740-S3458:::EHV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.54 | P23:345:OPPD:S3740-S3458:::EHV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.54 | Potential P4 Event - POI 645740_1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 132.46 | Potential P4 Event - POI 645740_7 | TDF Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 149.89 | Potential P4 Event - POI 645740_8 | TDF Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 156.81 | P12:345:OPPD:S3455-S3740:::EHV: | TDF Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 156.81 | P22:345:OPPD:S3455-S3740:::EHV: | TDF Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 156.81 | P23:345:OPPD:S3455-S3740:::EHV: | TDF Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 156.81 | Potential P4 Event - POI 645740_0 | TDF Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99998 | 147.02 | P41:345:OPPD:S3740-55&CC2:::EHV: | TDF Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99998 | 147.02 | P43:015-345:OPPD:S3740-S3455&CC2:::HV: | TDF Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99998 | 147.02 | P45:345:OPPD:S3740-S3455&CC2:::EHV: | TDF Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.54961 | 105.32 | P42:345:OPPD-LES:S3454-S3455&WAG:::EHV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.57209 | 113.2 | P42:345:MEC-OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.57209 | 113.2 | P45:345:OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.59009 | 111.84 | P12:345:OPPD:LX007::S3458.S3456.CKT1:: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.59407 | 106.09 | 635200 RAUN 3 345 762779 G18-043 TAP 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.59407 | 107.18 | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.59407 | 107.18 | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.59571 | 104.59 | P21:345:MEC-OPPD:AUTO-SINGLE:CBLUFFS3:S34563:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.6032 | 109.01 | P23:345:MEC:CBEC 905 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 106.69 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 106.69 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 106.83 | P23:345:MEC:ATCHISON CO 903 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 107.07 | 635017 ATCHISON 3 345 635018 WESTBORO 3 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 107.34 | Potential P4 Event - POI 635018_0 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 107.34 | Potential P4 Event - POI 635018_1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 107.34 | Potential P4 Event - POI 635018_2 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 107.74 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60424 | 105.07 | P23:345:AMMO::MAYWOOD:V33:: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60432 | 104.34 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60432 | 104.68 | P23:345:AMMO:::24SPENCERCREEK:EHV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60446 | 104.24 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60475 | 104.37 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60488 | 104.34 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.6049 | 108.85 | P23:345:MEC:CBEC 908 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60492 | 104.23 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60492 | 104.38 | P12:345:WERE:N345-AECI-345:::EHV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60493 | 104.25 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60495 | 104.29 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60495 | 104.29 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60495 | 104.3 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60496 | 104.39 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60496 | 104.39 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60496 | 104.39 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60497 | 104.14 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60497 | 104.19 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60497 | 104.26 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.15 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.17 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.18 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.19 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.42 | P12:500:EES-EAI:DRIVER:SHELBY | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.42 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.49 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.49 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.03 | 515853 DGRASSE4 138 763769 GEN-2019-045 138 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.11 | 520826 BENNGTN4 138 521115 BENNSUB4 138 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.11 | P12:HV:EES::3VIENNA_LA!:3RUSTON:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.11 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.12 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.12 | 514722 CLEVETP2 69.0 514723 CLEVLND2 69.0 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.14 | 515149 MADINDT4 138 515158 MADLIND4 138 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 346093 2LATHROP 69.0 344923 5LATHROP 161 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 523143 NP-PERDUR_G3 115 523186 SPEARMAN 3 115 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 523186 SPEARMAN 3 115 3WXFMR VON 13770/1 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 525731 SP-ABNTYPOI2 69.0 525816 TUCO_INT2 2 69.0 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.16 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.17 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.19 | 509829 FULTONW4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.22 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.23 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.25 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.26 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.26 | P12:161:OKGE:BKRBKR197:::: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.3 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.33 | 635580 ARBOR HILL 3 345 635582 ARBR HL B2 9 34.5 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.33 | P12:HV:EES::6DRIVER%:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.37 | 646211 S1211 5 161 645023 N OMA 3G 13.8 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.39 | P12:115:WERE:EMAN-KSU-115:::HV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.39 | P13:138-115:MP:TCH:TR4(1) | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.42 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.42 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.44 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.48 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.5 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.56 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.57 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.57 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.59 | P13:NBEC#1 GSU | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.63 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.68 | P13:SH902T GSU | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.69 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.7 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.72 | 762712 G18-037-TAP 161 762713 GEN-2018-037 161 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.72 | P11:18:SPC: BD #6+SSL:::HV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.77 | P11:18:SPC: BD #6:::HV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.79 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.8 | P11:024:DPC:ALMA2:6 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.91 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.99 | 764601 G20-025-GEN1 20.0 764600 GEN-2020-025 161 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.99 | 775961 GEN-2023-199 230 775962 G23-199XFMR1 34.5 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.99 | GEN-2020-028_POI_646363_Generator_outage | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.99 | GEN-2023-199_POI_640386_Generator_outage | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.04 | 762779 G18-043 TAP 345 762780 GEN-2018-043 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.08 | 764661 G20-031-GEN1 20.0 764660 GEN-2020-031 161 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.08 | GEN-2020-031_POI_646363_Generator_outage | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.24 | P11:115:XEL:HBR #6 7 8 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.25 | P11:20:XEL:AUTO-SINGLE:KING31G:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.28 | P23:345:XEL:8H14 PRI | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.3 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.3 | P23:345:XEL:8H17 PRI AS | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.35 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.48 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.49 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.5 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.54 | P23:345:XEL:8N8 MNN | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.58 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.58 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.9 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 106.01 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 106.23 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 106.83 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 106.98 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 108.9 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 109.21 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 109.42 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 110.09 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.605 | 104.19 | 344536 7ENON_TP 345 345217 7ROOTBEER 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.605 | 104.2 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60504 | 104.34 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60506 | 104.17 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60509 | 104.21 | 532791 BENTON 7 345 766141 G21-096-TAP 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60511 | 104.13 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60511 | 104.28 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60555 | 104.6 | 767240 G22-013-TAP 345 776600 G23-231-TAP 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60555 | 104.95 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60566 | 104.26 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.6057 | 105.04 | 300076 5FAIRPTB2 161 301559 5FAIRPTXF3 161 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.6057 | 105.04 | 301559 5FAIRPTXF3 161 300039 7FAIRPT 345 3 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60601 | 104.24 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60648 | 104.75 | 300039 7FAIRPT 345 640139 COOPER 3 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.6074 | 108.19 | P42:345:NPPD:BKR-CPR-3304:::: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.57 | Potential P4 Event - POI 541510_3 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.78 | Potential P4 Event - POI 541510_1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.8 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.82 | 541197 MULLNCR7 345 541510 HOLT 7 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.82 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.82 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.87 | 541197 MULLNCR7 345 771140 G22-208-TAP 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61786 | 106.38 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61786 | 106.39 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61786 | 106.45 | Potential P4 Event - POI 541510_0 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 119.18 | Potential P4 Event - POI 645740_10 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 134.5 | Potential P4 Event - POI 645740_11 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.54 | P12:345:OPPD:LX008::S3458.S3740.CKT1:: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.54 | P22:345:OPPD:S3458-S3740:::EHV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.54 | P22:345:OPPD:S3740-S3458:::EHV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.54 | P23:345:OPPD:S3740-S3458:::EHV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.54 | Potential P4 Event - POI 645740_1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 132.46 | Potential P4 Event - POI 645740_7 | TDF Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 149.89 | Potential P4 Event - POI 645740_8 | TDF Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 156.81 | P12:345:OPPD:S3455-S3740:::EHV: | TDF Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 156.81 | P22:345:OPPD:S3455-S3740:::EHV: | TDF Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 156.81 | P23:345:OPPD:S3455-S3740:::EHV: | TDF Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 156.81 | Potential P4 Event - POI 645740_0 | TDF Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99998 | 147.02 | P41:345:OPPD:S3740-55&CC2:::EHV: | TDF Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99998 | 147.02 | P43:015-345:OPPD:S3740-S3455&CC2:::HV: | TDF Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99998 | 147.02 | P45:345:OPPD:S3740-S3455&CC2:::EHV: | TDF Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.54961 | 105.32 | P42:345:OPPD-LES:S3454-S3455&WAG:::EHV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.57209 | 113.2 | P42:345:MEC-OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.57209 | 113.2 | P45:345:OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.59009 | 111.84 | P12:345:OPPD:LX007::S3458.S3456.CKT1:: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.59407 | 106.09 | 635200 RAUN 3 345 762779 G18-043 TAP 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.59407 | 107.18 | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.59407 | 107.18 | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.59571 | 104.59 | P21:345:MEC-OPPD:AUTO-SINGLE:CBLUFFS3:S34563:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.6032 | 109.01 | P23:345:MEC:CBEC 905 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 106.69 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 106.69 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 106.83 | P23:345:MEC:ATCHISON CO 903 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 107.07 | 635017 ATCHISON 3 345 635018 WESTBORO 3 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 107.34 | Potential P4 Event - POI 635018_0 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 107.34 | Potential P4 Event - POI 635018_1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 107.34 | Potential P4 Event - POI 635018_2 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 107.74 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60424 | 105.07 | P23:345:AMMO::MAYWOOD:V33:: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60432 | 104.34 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60432 | 104.68 | P23:345:AMMO:::24SPENCERCREEK:EHV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60446 | 104.24 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60475 | 104.37 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60488 | 104.34 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.6049 | 108.85 | P23:345:MEC:CBEC 908 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60492 | 104.23 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60492 | 104.38 | P12:345:WERE:N345-AECI-345:::EHV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60493 | 104.25 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60495 | 104.29 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60495 | 104.29 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60495 | 104.3 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60496 | 104.39 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60496 | 104.39 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60496 | 104.39 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60497 | 104.14 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60497 | 104.19 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60497 | 104.26 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.15 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.17 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.18 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.19 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.42 | P12:500:EES-EAI:DRIVER:SHELBY | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.42 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.49 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.49 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.03 | 515853 DGRASSE4 138 763769 GEN-2019-045 138 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.11 | 520826 BENNGTN4 138 521115 BENNSUB4 138 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.11 | P12:HV:EES::3VIENNA_LA!:3RUSTON:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.11 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.12 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.12 | 514722 CLEVETP2 69.0 514723 CLEVLND2 69.0 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.14 | 515149 MADINDT4 138 515158 MADLIND4 138 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 346093 2LATHROP 69.0 344923 5LATHROP 161 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 523143 NP-PERDUR_G3 115 523186 SPEARMAN 3 115 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 523186 SPEARMAN 3 115 3WXFMR VON 13770/1 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 525731 SP-ABNTYPOI2 69.0 525816 TUCO_INT2 2 69.0 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.16 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.17 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.19 | 509829 FULTONW4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.22 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.23 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.25 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.26 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.26 | P12:161:OKGE:BKRBKR197:::: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.3 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.33 | 635580 ARBOR HILL 3 345 635582 ARBR HL B2 9 34.5 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.33 | P12:HV:EES::6DRIVER%:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.37 | 646211 S1211 5 161 645023 N OMA 3G 13.8 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.39 | P12:115:WERE:EMAN-KSU-115:::HV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.39 | P13:138-115:MP:TCH:TR4(1) | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.42 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.42 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.44 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.48 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.5 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.56 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.57 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.57 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.59 | P13:NBEC#1 GSU | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.63 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.68 | P13:SH902T GSU | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.69 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.7 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.72 | 762712 G18-037-TAP 161 762713 GEN-2018-037 161 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.72 | P11:18:SPC: BD #6+SSL:::HV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.77 | P11:18:SPC: BD #6:::HV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.79 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.8 | P11:024:DPC:ALMA2:6 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.91 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.99 | 764601 G20-025-GEN1 20.0 764600 GEN-2020-025 161 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.99 | 775961 GEN-2023-199 230 775962 G23-199XFMR1 34.5 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.99 | GEN-2020-028_POI_646363_Generator_outage | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.99 | GEN-2023-199_POI_640386_Generator_outage | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.04 | 762779 G18-043 TAP 345 762780 GEN-2018-043 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.08 | 764661 G20-031-GEN1 20.0 764660 GEN-2020-031 161 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.08 | GEN-2020-031_POI_646363_Generator_outage | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.24 | P11:115:XEL:HBR #6 7 8 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.25 | P11:20:XEL:AUTO-SINGLE:KING31G:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.28 | P23:345:XEL:8H14 PRI | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.3 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.3 | P23:345:XEL:8H17 PRI AS | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.35 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.48 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.49 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.5 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.54 | P23:345:XEL:8N8 MNN | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.58 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.58 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.9 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 106.01 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 106.23 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 106.83 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 106.98 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 108.9 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 109.21 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 109.42 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 110.09 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.605 | 104.19 | 344536 7ENON_TP 345 345217 7ROOTBEER 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.605 | 104.2 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60504 | 104.34 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60506 | 104.17 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60509 | 104.21 | 532791 BENTON 7 345 766141 G21-096-TAP 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60511 | 104.13 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60511 | 104.28 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60555 | 104.6 | 767240 G22-013-TAP 345 776600 G23-231-TAP 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60555 | 104.95 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60566 | 104.26 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.6057 | 105.04 | 300076 5FAIRPTB2 161 301559 5FAIRPTXF3 161 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.6057 | 105.04 | 301559 5FAIRPTXF3 161 300039 7FAIRPT 345 3 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60601 | 104.24 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60648 | 104.75 | 300039 7FAIRPT 345 640139 COOPER 3 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.6074 | 108.19 | P42:345:NPPD:BKR-CPR-3304:::: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.57 | Potential P4 Event - POI 541510_3 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.78 | Potential P4 Event - POI 541510_1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.8 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.82 | 541197 MULLNCR7 345 541510 HOLT 7 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.82 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.82 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.87 | 541197 MULLNCR7 345 771140 G22-208-TAP 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61786 | 106.38 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61786 | 106.39 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61786 | 106.45 | Potential P4 Event - POI 541510_0 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 119.18 | Potential P4 Event - POI 645740_10 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 134.5 | Potential P4 Event - POI 645740_11 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.54 | P12:345:OPPD:LX008::S3458.S3740.CKT1:: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.54 | P22:345:OPPD:S3458-S3740:::EHV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.54 | P22:345:OPPD:S3740-S3458:::EHV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.54 | P23:345:OPPD:S3740-S3458:::EHV: | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.54 | Potential P4 Event - POI 645740_1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 132.46 | Potential P4 Event - POI 645740_7 | TDF Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 149.89 | Potential P4 Event - POI 645740_8 | TDF Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 156.81 | P12:345:OPPD:S3455-S3740:::EHV: | TDF Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 156.81 | P22:345:OPPD:S3455-S3740:::EHV: | TDF Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 156.81 | P23:345:OPPD:S3455-S3740:::EHV: | TDF Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 156.81 | Potential P4 Event - POI 645740_0 | TDF Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99998 | 147.02 | P41:345:OPPD:S3740-55&CC2:::EHV: | TDF Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99998 | 147.02 | P43:015-345:OPPD:S3740-S3455&CC2:::HV: | TDF Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99998 | 147.02 | P45:345:OPPD:S3740-S3455&CC2:::EHV: | TDF Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | 193 | 193 | 0.27216 | 140.8 | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 193 | 193 | 0.22811 | 101.78 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 193 | 193 | 0.27331 | 141.4 | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.23425 | 177.76 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.23425 | 179.69 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.23425 | 179.94 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.26657 | 200.2 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.29875 | 141.91 | GEN-2023-225_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31104 | 141 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31135 | 141.21 | Potential P4 Event - POI 640226_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31142 | 140.27 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.75 | P23:345:AMMO::MAYWOOD:V33:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31146 | 140.26 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31147 | 142.07 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 140.24 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 140.38 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 140.44 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 140.45 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 140.46 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 140.54 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 140.8 | P23:345:MEC:LOUISA 964 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 141.25 | Potential P4 Event - POI 640226_3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 141.96 | Potential P4 Event - POI 640226_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.81 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.92 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.92 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.95 | 515802 GRACMNT4 138 774981 GEN-2023-150 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.96 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.96 | 515543 RENFROW7 345 760809 GEN-2017-203 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.96 | 655845 GRDNCRK2-MK7 115 655879 OASIS___-MK7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.97 | 514801 MINCO 7 345 761250 GEN-2017-233 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.97 | 523267 PRINGLE 6 230 774441 GEN-2023-123 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.97 | 523309 MOORE_CNTY 6 230 772181 GEN-2023-010 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.97 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.97 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.18 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.18 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.18 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.18 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.19 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.19 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.2 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.2 | 509829 FULTONW4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.21 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.21 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.21 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.22 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.24 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.25 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.26 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.27 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.27 | P12:138:OKGE:BKRBKR176:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.27 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.28 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.28 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.33 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.34 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.34 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.34 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.35 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.35 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.39 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.39 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.4 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.41 | 48983 J1898 SUB 161 3WXFMR J1898 SUB 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.41 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.41 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.41 | P23:500:EES:PERVIL:R9872 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.41 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.42 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.44 | 51993 J2199 SUB 345 3WXFMR J2199 SUB 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.45 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.45 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.5 | 762779 G18-043 TAP 345 762780 GEN-2018-043 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.53 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER 3.:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.56 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.56 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.56 | P13:NBEC#1 GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.57 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.58 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.64 | P13:SH902T GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.67 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.67 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.67 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.67 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.68 | P11:18:SPC: BD #6+SSL:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.72 | P11:18:SPC: BD #6:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.79 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.88 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.05 | P11:115:XEL:HBR #6 7 8 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.07 | P23:345:XEL:8H14 PRI | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.08 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.09 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.13 | GEN-2021-043_POI_650290_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.26 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.27 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.27 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.27 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.27 | P23:345:XEL:8N22 SHC | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.3 | 640427 STEELEC9 4.16 640426 STEELEC7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.31 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.35 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.35 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.37 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.45 | P23:345:OPPD:S3740-S3455&CC2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.45 | P41:345:OPPD:S3740-55&CC2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.45 | P42:345:OPPD:S3740-S3455&CC2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.45 | P43:015-345:OPPD:S3740-S3455&CC2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.59 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.61 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.71 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.91 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.94 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.95 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.01 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.05 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.11 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.11 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.11 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.11 | Potential P4 Event - POI 640590_12 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.11 | Potential P4 Event - POI 640590_13 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.18 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.26 | Potential P4 Event - POI 645740_6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.3 | Potential P4 Event - POI 645740_12 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.41 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 143.96 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 144.16 | GEN-2023-224_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 144.16 | Potential P4 Event - POI 640590_9 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 146.12 | Potential P4 Event - POI 645740_5 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 146.58 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3115 | 140.24 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3115 | 140.25 | 512694 CLEVLND7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3115 | 140.44 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3115 | 140.48 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31151 | 140.18 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31151 | 140.53 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31151 | 140.57 | P42:345:OKGE:SB_SOER7383:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31153 | 140.34 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31154 | 140.35 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31154 | 140.43 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31167 | 140.3 | P12:115:HAST:::LINE | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31233 | 141.42 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31276 | 140.7 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31276 | 140.72 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31552 | 141.97 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31552 | 142.1 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31621 | 141.76 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31621 | 142.62 | P12:115:WERE:KNOB-MKEC-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31621 | 142.64 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.32883 | 154.35 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34903 | 157.75 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34903 | 157.75 | P13:115-161:NPPD:HUMBOLT5:T2::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34903 | 159.08 | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34903 | 159.51 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34903 | 159.53 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.37286 | 175.27 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.55406 | 247.71 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.38615 | 132.39 | GEN-2023-225_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40204 | 131.52 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40244 | 131.71 | Potential P4 Event - POI 640226_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40253 | 130.82 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40257 | 130.81 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40257 | 131.28 | P23:345:AMMO::MAYWOOD:V33:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40259 | 132.54 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4026 | 131.01 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4026 | 131.33 | P23:345:MEC:LOUISA 964 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4026 | 132.43 | Potential P4 Event - POI 640226_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40261 | 130.79 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40261 | 130.81 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40261 | 130.93 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40261 | 130.99 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40261 | 130.99 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40261 | 131.08 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40261 | 131.76 | Potential P4 Event - POI 640226_3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 129.76 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.38 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.49 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.49 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.51 | 508563 PIRKEY 7 345 769761 GEN-2022-139 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.52 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.52 | 507751 RDPOINT4 138 776581 GEN-2023-230 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.52 | 515802 GRACMNT4 138 774981 GEN-2023-150 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.53 | 514801 MINCO 7 345 761250 GEN-2017-233 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.53 | 515543 RENFROW7 345 760809 GEN-2017-203 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.53 | 523267 PRINGLE 6 230 774441 GEN-2023-123 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.53 | 523309 MOORE_CNTY 6 230 772181 GEN-2023-010 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.53 | 655845 GRDNCRK2-MK7 115 655879 OASIS___-MK7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.73 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.73 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.74 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.75 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.75 | 509829 FULTONW4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.75 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.76 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.76 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.76 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.77 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.79 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.81 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.82 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.82 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.83 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.83 | P12:138:OKGE:BKRBKR176:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.83 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.88 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.88 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.88 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.89 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.9 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.9 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.93 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.93 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.95 | 48983 J1898 SUB 161 3WXFMR J1898 SUB 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.95 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.96 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.96 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.96 | P23:500:EES:PERVIL:R9872 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.96 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.96 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.98 | 51993 J2199 SUB 345 3WXFMR J2199 SUB 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.99 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.04 | 762779 G18-043 TAP 345 762780 GEN-2018-043 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.07 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.1 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.1 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.1 | P13:NBEC#1 GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.11 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.12 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.18 | P13:SH902T GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.2 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.2 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.21 | P11:18:SPC: BD #6+SSL:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.21 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.21 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.25 | P11:18:SPC: BD #6:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.32 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.41 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.56 | P11:115:XEL:HBR #6 7 8 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.59 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.59 | P23:345:XEL:8H14 PRI | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.61 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.64 | GEN-2021-043_POI_650290_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.77 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.77 | P23:345:XEL:8N22 SHC | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.78 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.78 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.78 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.81 | 640427 STEELEC9 4.16 640426 STEELEC7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.82 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.85 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.85 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.87 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.93 | P23:345:OPPD:S3740-S3455&CC2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.93 | P41:345:OPPD:S3740-55&CC2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.93 | P42:345:OPPD:S3740-S3455&CC2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.93 | P43:015-345:OPPD:S3740-S3455&CC2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.08 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.1 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.2 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.39 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.42 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.43 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.48 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.53 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.58 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.58 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.58 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.58 | Potential P4 Event - POI 640590_10 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.58 | Potential P4 Event - POI 640590_12 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.65 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.71 | Potential P4 Event - POI 645740_6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.77 | Potential P4 Event - POI 645740_12 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.87 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 134.35 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 134.54 | GEN-2023-224_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 134.54 | Potential P4 Event - POI 640590_9 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 136.42 | Potential P4 Event - POI 645740_5 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 136.86 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40263 | 130.79 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40263 | 130.8 | 512694 CLEVLND7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40263 | 130.98 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40263 | 131.02 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40264 | 130.74 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40264 | 131.07 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40264 | 131.11 | P42:345:OKGE:SB_SOER7383:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40267 | 130.89 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40269 | 130.9 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40269 | 130.97 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40285 | 130.85 | P12:115:HAST:::LINE | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40371 | 131.92 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40426 | 131.24 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40426 | 131.26 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40783 | 132.45 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40783 | 132.57 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40872 | 132.25 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40873 | 133.07 | P12:115:WERE:KNOB-MKEC-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40873 | 133.09 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.42503 | 144.29 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45114 | 147.56 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45114 | 149.24 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45114 | 149.25 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.48194 | 164.34 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60884 | 194.13 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60884 | 197.29 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60884 | 197.55 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 771999 G23-222-POI 345 776422 G23-222XFMR1 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 771999 G23-222-POI 345 776425 G23-222XFMR2 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 771999 G23-222-POI 345 776442 G23-223XFMR1 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 776422 G23-222XFMR1 345 776424 G23-222GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 776425 G23-222XFMR2 345 776427 G23-222GEN2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 776442 G23-223XFMR1 345 776444 G23-223GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.29875 | 138.37 | GEN-2023-225_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31104 | 137.45 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31135 | 137.65 | Potential P4 Event - POI 640226_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31142 | 136.7 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.19 | P23:345:AMMO::MAYWOOD:V33:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31146 | 136.7 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31147 | 138.54 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 136.68 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 136.82 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 136.88 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 136.89 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 136.9 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 136.98 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 137.25 | P23:345:MEC:LOUISA 964 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 137.7 | Potential P4 Event - POI 640226_3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 138.42 | Potential P4 Event - POI 640226_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.23 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.35 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.35 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.38 | 515802 GRACMNT4 138 774981 GEN-2023-150 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.39 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.39 | 515543 RENFROW7 345 760809 GEN-2017-203 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.4 | 514801 MINCO 7 345 761250 GEN-2017-233 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.4 | 523267 PRINGLE 6 230 774441 GEN-2023-123 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.4 | 523309 MOORE_CNTY 6 230 772181 GEN-2023-010 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.4 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.4 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.41 | 655846 F9______-MK7 115 655872 G9TAP___-MK7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.61 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.61 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.61 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.61 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.62 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.63 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.63 | 509829 FULTONW4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.63 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.64 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.65 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.65 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.65 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.67 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.69 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.7 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.71 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.71 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.71 | P12:138:OKGE:BKRBKR176:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.71 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.71 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.77 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.77 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.77 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.78 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.79 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.79 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.83 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.83 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.84 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.85 | 48983 J1898 SUB 161 3WXFMR J1898 SUB 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.85 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.85 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.85 | P23:500:EES:PERVIL:R9872 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.85 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.86 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.88 | 51993 J2199 SUB 345 3WXFMR J2199 SUB 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.89 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.89 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.94 | 762779 G18-043 TAP 345 762780 GEN-2018-043 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.97 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137 | P13:NBEC#1 GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.01 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.01 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.01 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.02 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.09 | P13:SH902T GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.11 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.11 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.12 | P11:18:SPC: BD #6+SSL:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.12 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.12 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.17 | P11:18:SPC: BD #6:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.23 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.33 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.5 | P11:115:XEL:HBR #6 7 8 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.52 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.53 | P23:345:XEL:8H14 PRI | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.55 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.58 | GEN-2021-043_POI_650290_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.72 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.72 | P23:345:XEL:8N22 SHC | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.73 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.73 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.73 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.77 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.8 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.8 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.83 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.87 | P23:345:OPPD:S3740-S3455&CC2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.87 | P41:345:OPPD:S3740-55&CC2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.87 | P42:345:OPPD:S3740-S3455&CC2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.87 | P43:015-345:OPPD:S3740-S3455&CC2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.05 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.07 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.17 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.37 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.41 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.42 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.48 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.52 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.58 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.58 | Potential P4 Event - POI 640590_10 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.58 | Potential P4 Event - POI 640590_11 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.59 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.59 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.65 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.7 | Potential P4 Event - POI 645740_6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.78 | Potential P4 Event - POI 645740_12 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.88 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 140.43 | 640112 CLATONA9 34.5 3WXFMR CLATONIA T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 140.47 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 140.67 | GEN-2023-224_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 140.67 | Potential P4 Event - POI 640590_9 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 142.67 | Potential P4 Event - POI 645740_5 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 143.13 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3115 | 136.68 | 512694 CLEVLND7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3115 | 136.68 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3115 | 136.88 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3115 | 136.92 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31151 | 136.62 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31151 | 136.97 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31151 | 137.01 | P42:345:OKGE:SB_SOER7383:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31153 | 136.78 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31154 | 136.79 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31154 | 136.87 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31167 | 136.74 | P12:115:HAST:::LINE | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31233 | 137.88 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31276 | 137.15 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31276 | 137.17 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31552 | 138.44 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31552 | 138.57 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31621 | 138.23 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31621 | 139.1 | P12:115:WERE:KNOB-MKEC-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31621 | 139.12 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.32883 | 151.05 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34903 | 154.53 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34903 | 154.53 | P13:115-161:NPPD:HUMBOLT5:T2::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34903 | 155.88 | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34903 | 156.33 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34903 | 156.34 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.37286 | 172.43 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.55406 | 246.37 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 771999 G23-222-POI 345 776422 G23-222XFMR1 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 771999 G23-222-POI 345 776425 G23-222XFMR2 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 771999 G23-222-POI 345 776442 G23-223XFMR1 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 776422 G23-222XFMR1 345 776424 G23-222GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 776425 G23-222XFMR2 345 776427 G23-222GEN2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 776442 G23-223XFMR1 345 776444 G23-223GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | 193 | 193 | 0.27216 | 140.8 | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 193 | 193 | 0.22811 | 101.78 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 193 | 193 | 0.27331 | 141.4 | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.23425 | 177.76 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.23425 | 179.69 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.23425 | 179.94 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.26657 | 200.2 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.29875 | 141.91 | GEN-2023-225_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31104 | 141 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31135 | 141.21 | Potential P4 Event - POI 640226_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31142 | 140.27 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.75 | P23:345:AMMO::MAYWOOD:V33:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31146 | 140.26 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31147 | 142.07 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 140.24 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 140.38 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 140.44 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 140.45 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 140.46 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 140.54 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 140.8 | P23:345:MEC:LOUISA 964 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 141.25 | Potential P4 Event - POI 640226_3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 141.96 | Potential P4 Event - POI 640226_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.81 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.92 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.92 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.95 | 515802 GRACMNT4 138 774981 GEN-2023-150 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.96 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.96 | 515543 RENFROW7 345 760809 GEN-2017-203 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.96 | 655845 GRDNCRK2-MK7 115 655879 OASIS___-MK7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.97 | 514801 MINCO 7 345 761250 GEN-2017-233 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.97 | 523267 PRINGLE 6 230 774441 GEN-2023-123 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.97 | 523309 MOORE_CNTY 6 230 772181 GEN-2023-010 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.97 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.97 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.18 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.18 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.18 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.18 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.19 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.19 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.2 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.2 | 509829 FULTONW4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.21 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.21 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.21 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.22 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.24 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.25 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.26 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.27 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.27 | P12:138:OKGE:BKRBKR176:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.27 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.28 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.28 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.33 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.34 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.34 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.34 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.35 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.35 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.39 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.39 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.4 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.41 | 48983 J1898 SUB 161 3WXFMR J1898 SUB 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.41 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.41 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.41 | P23:500:EES:PERVIL:R9872 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.41 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.42 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.44 | 51993 J2199 SUB 345 3WXFMR J2199 SUB 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.45 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.45 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.5 | 762779 G18-043 TAP 345 762780 GEN-2018-043 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.53 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.56 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.56 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.56 | P13:NBEC#1 GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.57 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.58 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.64 | P13:SH902T GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.67 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.67 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.67 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.67 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.68 | P11:18:SPC: BD #6+SSL:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.72 | P11:18:SPC: BD #6:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.79 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.88 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.05 | P11:115:XEL:HBR #6 7 8 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.07 | P23:345:XEL:8H14 PRI | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.08 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.09 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.13 | GEN-2021-043_POI_650290_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.26 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.27 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.27 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.27 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.27 | P23:345:XEL:8N22 SHC | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.3 | 640427 STEELEC9 4.16 640426 STEELEC7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.31 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.35 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.35 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.37 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.45 | P23:345:OPPD:S3740-S3455&CC2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.45 | P41:345:OPPD:S3740-55&CC2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.45 | P42:345:OPPD:S3740-S3455&CC2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.45 | P43:015-345:OPPD:S3740-S3455&CC2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.59 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.61 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.71 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.91 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.94 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.95 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.01 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.05 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.11 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.11 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.11 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.11 | Potential P4 Event - POI 640590_12 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.11 | Potential P4 Event - POI 640590_13 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.18 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.26 | Potential P4 Event - POI 645740_6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.3 | Potential P4 Event - POI 645740_12 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.41 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 143.96 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 144.16 | GEN-2023-224_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 144.16 | Potential P4 Event - POI 640590_9 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 146.12 | Potential P4 Event - POI 645740_5 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 146.58 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3115 | 140.24 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3115 | 140.25 | 512694 CLEVLND7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3115 | 140.44 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3115 | 140.48 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31151 | 140.18 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31151 | 140.53 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31151 | 140.57 | P42:345:OKGE:SB_SOER7383:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31153 | 140.34 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31154 | 140.35 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31154 | 140.43 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31167 | 140.3 | P12:115:HAST:::LINE | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31233 | 141.42 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31276 | 140.7 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31276 | 140.72 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31552 | 141.97 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31552 | 142.1 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31621 | 141.76 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31621 | 142.62 | P12:115:WERE:KNOB-MKEC-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31621 | 142.64 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.32883 | 154.35 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34903 | 157.75 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34903 | 157.75 | P13:115-161:NPPD:HUMBOLT5:T2::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34903 | 159.08 | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34903 | 159.51 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34903 | 159.53 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.37286 | 175.27 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.55406 | 247.71 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.38615 | 132.39 | GEN-2023-225_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40204 | 131.52 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40244 | 131.71 | Potential P4 Event - POI 640226_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40253 | 130.82 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40257 | 130.81 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40257 | 131.28 | P23:345:AMMO::MAYWOOD:V33:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40259 | 132.54 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4026 | 131.01 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4026 | 131.33 | P23:345:MEC:LOUISA 964 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4026 | 132.43 | Potential P4 Event - POI 640226_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40261 | 130.79 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40261 | 130.81 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40261 | 130.93 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40261 | 130.99 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40261 | 130.99 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40261 | 131.08 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40261 | 131.76 | Potential P4 Event - POI 640226_3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 129.76 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.38 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.49 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.49 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.51 | 508563 PIRKEY 7 345 769761 GEN-2022-139 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.52 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.52 | 507751 RDPOINT4 138 776581 GEN-2023-230 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.52 | 515802 GRACMNT4 138 774981 GEN-2023-150 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.53 | 514801 MINCO 7 345 761250 GEN-2017-233 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.53 | 515543 RENFROW7 345 760809 GEN-2017-203 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.53 | 523267 PRINGLE 6 230 774441 GEN-2023-123 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.53 | 523309 MOORE_CNTY 6 230 772181 GEN-2023-010 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.53 | 655845 GRDNCRK2-MK7 115 655879 OASIS___-MK7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.73 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.73 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.74 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.75 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.75 | 509829 FULTONW4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.75 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.76 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.76 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.76 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.77 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.79 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.81 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.82 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.82 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.83 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.83 | P12:138:OKGE:BKRBKR176:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.83 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.88 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.88 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.88 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.89 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.9 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.9 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.93 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.93 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.95 | 48983 J1898 SUB 161 3WXFMR J1898 SUB 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.95 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.96 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.96 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.96 | P23:500:EES:PERVIL:R9872 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.96 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.96 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.98 | 51993 J2199 SUB 345 3WXFMR J2199 SUB 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.99 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.04 | 762779 G18-043 TAP 345 762780 GEN-2018-043 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.07 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.1 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.1 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.1 | P13:NBEC#1 GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.11 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.12 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.18 | P13:SH902T GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.2 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.2 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.21 | P11:18:SPC: BD #6+SSL:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.21 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.21 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.25 | P11:18:SPC: BD #6:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.32 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.41 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.56 | P11:115:XEL:HBR #6 7 8 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.59 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.59 | P23:345:XEL:8H14 PRI | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.61 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.64 | GEN-2021-043_POI_650290_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.77 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.77 | P23:345:XEL:8N22 SHC | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.78 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.78 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.78 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.81 | 640427 STEELEC9 4.16 640426 STEELEC7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.82 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.85 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.85 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.87 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.93 | P23:345:OPPD:S3740-S3455&CC2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.93 | P41:345:OPPD:S3740-55&CC2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.93 | P42:345:OPPD:S3740-S3455&CC2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.93 | P43:015-345:OPPD:S3740-S3455&CC2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.08 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.1 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.2 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.39 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.42 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.43 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.48 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.53 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.58 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.58 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.58 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.58 | Potential P4 Event - POI 640590_10 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.58 | Potential P4 Event - POI 640590_12 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.65 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.71 | Potential P4 Event - POI 645740_6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.77 | Potential P4 Event - POI 645740_12 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.87 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 134.35 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 134.54 | GEN-2023-224_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 134.54 | Potential P4 Event - POI 640590_9 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 136.42 | Potential P4 Event - POI 645740_5 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 136.86 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40263 | 130.79 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40263 | 130.8 | 512694 CLEVLND7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40263 | 130.98 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40263 | 131.02 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40264 | 130.74 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40264 | 131.07 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40264 | 131.11 | P42:345:OKGE:SB_SOER7383:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40267 | 130.89 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40269 | 130.9 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40269 | 130.97 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40285 | 130.85 | P12:115:HAST:::LINE | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40371 | 131.92 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40426 | 131.24 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40426 | 131.26 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40783 | 132.45 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40783 | 132.57 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40872 | 132.25 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40873 | 133.07 | P12:115:WERE:KNOB-MKEC-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40873 | 133.09 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.42503 | 144.29 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45114 | 147.56 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45114 | 149.24 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45114 | 149.25 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.48194 | 164.34 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60884 | 194.13 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60884 | 197.29 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60884 | 197.55 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 771999 G23-222-POI 345 776422 G23-222XFMR1 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 771999 G23-222-POI 345 776425 G23-222XFMR2 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 776422 G23-222XFMR1 345 776424 G23-222GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 776425 G23-222XFMR2 345 776427 G23-222GEN2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.29875 | 138.37 | GEN-2023-225_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31104 | 137.45 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31135 | 137.65 | Potential P4 Event - POI 640226_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31142 | 136.7 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.19 | P23:345:AMMO::MAYWOOD:V33:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31146 | 136.7 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31147 | 138.54 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 136.68 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 136.82 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 136.88 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 136.89 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 136.9 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 136.98 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 137.25 | P23:345:MEC:LOUISA 964 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 137.7 | Potential P4 Event - POI 640226_3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 138.42 | Potential P4 Event - POI 640226_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.23 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.35 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.35 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.38 | 515802 GRACMNT4 138 774981 GEN-2023-150 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.39 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.39 | 515543 RENFROW7 345 760809 GEN-2017-203 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.4 | 514801 MINCO 7 345 761250 GEN-2017-233 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.4 | 523267 PRINGLE 6 230 774441 GEN-2023-123 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.4 | 523309 MOORE_CNTY 6 230 772181 GEN-2023-010 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.4 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.4 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.41 | 655846 F9______-MK7 115 655872 G9TAP___-MK7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.61 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.61 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.61 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.61 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.62 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.63 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.63 | 509829 FULTONW4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.63 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.64 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.65 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.65 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.65 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.67 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.69 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.7 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.71 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.71 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.71 | P12:138:OKGE:BKRBKR176:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.71 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.71 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.77 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.77 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.77 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.78 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.79 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.79 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.83 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.83 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.84 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.85 | 48983 J1898 SUB 161 3WXFMR J1898 SUB 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.85 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.85 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.85 | P23:500:EES:PERVIL:R9872 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.85 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.86 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.88 | 51993 J2199 SUB 345 3WXFMR J2199 SUB 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.89 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.89 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.94 | 762779 G18-043 TAP 345 762780 GEN-2018-043 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.97 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137 | P13:NBEC#1 GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.01 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.01 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.01 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.02 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.09 | P13:SH902T GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.11 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.11 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.12 | P11:18:SPC: BD #6+SSL:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.12 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.12 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.17 | P11:18:SPC: BD #6:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.23 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.33 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.5 | P11:115:XEL:HBR #6 7 8 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.52 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.53 | P23:345:XEL:8H14 PRI | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.55 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.58 | GEN-2021-043_POI_650290_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.72 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.72 | P23:345:XEL:8N22 SHC | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.73 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.73 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.73 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.77 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.8 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.8 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.83 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.87 | P23:345:OPPD:S3740-S3455&CC2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.87 | P41:345:OPPD:S3740-55&CC2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.87 | P42:345:OPPD:S3740-S3455&CC2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.87 | P43:015-345:OPPD:S3740-S3455&CC2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.05 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.07 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.17 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.37 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.41 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.42 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.48 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.52 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.58 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.58 | Potential P4 Event - POI 640590_10 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.58 | Potential P4 Event - POI 640590_11 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.59 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.59 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.65 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.7 | Potential P4 Event - POI 645740_6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.78 | Potential P4 Event - POI 645740_12 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.88 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 140.43 | 640112 CLATONA9 34.5 3WXFMR CLATONIA T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 140.47 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 140.67 | GEN-2023-224_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 140.67 | Potential P4 Event - POI 640590_9 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 142.67 | Potential P4 Event - POI 645740_5 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 143.13 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3115 | 136.68 | 512694 CLEVLND7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3115 | 136.68 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3115 | 136.88 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3115 | 136.92 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31151 | 136.62 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31151 | 136.97 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31151 | 137.01 | P42:345:OKGE:SB_SOER7383:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31153 | 136.78 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31154 | 136.79 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31154 | 136.87 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31167 | 136.74 | P12:115:HAST:::LINE | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31233 | 137.88 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31276 | 137.15 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31276 | 137.17 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31552 | 138.44 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31552 | 138.57 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31621 | 138.23 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31621 | 139.1 | P12:115:WERE:KNOB-MKEC-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31621 | 139.12 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.32883 | 151.05 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34903 | 154.53 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34903 | 154.53 | P13:115-161:NPPD:HUMBOLT5:T2::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34903 | 155.88 | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34903 | 156.33 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34903 | 156.34 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.37286 | 172.43 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.55406 | 246.37 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 771999 G23-222-POI 345 776422 G23-222XFMR1 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 771999 G23-222-POI 345 776425 G23-222XFMR2 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 776422 G23-222XFMR1 345 776424 G23-222GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 776425 G23-222XFMR2 345 776427 G23-222GEN2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60581 | 103.06 | Potential P4 Event - POI 645740_4 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60581 | 106.7 | 645454 S3454 3 345 645740 S3740 3 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.66 | Potential P4 Event - POI 645740_1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-077 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 156.79 | Potential P4 Event - POI 645740_0 | TDF Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60581 | 103.06 | Potential P4 Event - POI 645740_4 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60581 | 106.7 | 645454 S3454 3 345 645740 S3740 3 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.66 | Potential P4 Event - POI 645740_1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-078 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 156.79 | Potential P4 Event - POI 645740_0 | TDF Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60581 | 103.06 | Potential P4 Event - POI 645740_4 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60581 | 106.7 | 645454 S3454 3 345 645740 S3740 3 345 1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.66 | Potential P4 Event - POI 645740_1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-079 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 156.79 | Potential P4 Event - POI 645740_0 | TDF Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | 193 | 193 | 0.27226 | 139.25 | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 193 | 193 | 0.22818 | 101.08 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 193 | 193 | 0.27341 | 139.83 | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.2343 | 175.6 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.2343 | 177.52 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.2343 | 177.77 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.26662 | 198.16 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.29874 | 142.9 | GEN-2023-225_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.311 | 142.19 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31131 | 142.19 | Potential P4 Event - POI 640226_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3114 | 141.82 | P23:345:AMMO::MAYWOOD:V33:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31141 | 141.33 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31142 | 143.08 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31143 | 141.27 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31143 | 141.46 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31143 | 141.84 | P23:345:MEC:LOUISA 964 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31143 | 142.27 | Potential P4 Event - POI 640226_3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31143 | 142.94 | Potential P4 Event - POI 640226_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 140.99 | 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 140.99 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.19 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.19 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.21 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.22 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.22 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.23 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.23 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.28 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.28 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.29 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.3 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.3 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.35 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.35 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.36 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.36 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.39 | 541198 PECULR 7 345 541200 PHILL 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.42 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.42 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.43 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.43 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.43 | P23:500:EES:PERVIL:R9872 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.43 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.44 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.47 | P41:345:OPPD:S3740-55&CC2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.47 | P42:345:OPPD:S3740-S3455&CC2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.47 | P43:015-345:OPPD:S3740-S3455&CC2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.57 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.64 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.64 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.79 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 142.03 | P23:345:XEL:8P2 KING | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 142.83 | Potential P4 Event - POI 645740_2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 142.96 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.93 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.94 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.96 | 514715 WOODRNG7 345 762321 GEN-2017-164 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.96 | 514787 DEWEY 4 138 766160 GEN-2021-098 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.97 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.97 | 515802 GRACMNT4 138 774981 GEN-2023-150 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.98 | 514801 MINCO 7 345 761250 GEN-2017-233 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.98 | 515543 RENFROW7 345 760809 GEN-2017-203 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.98 | 523267 PRINGLE 6 230 774441 GEN-2023-123 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.98 | 523309 MOORE_CNTY 6 230 772181 GEN-2023-010 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.99 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.99 | 655840 CHRRYCRK-MK7 115 655876 DPLWCTAP-MK7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.99 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.2 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.21 | 509829 FULTONW4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.21 | 511560 GRADY 4 138 511567 CHOCTAW4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.22 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.25 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.29 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.3 | P12:138:OKGE:BKRBKR176:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.35 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.36 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.42 | 640278 SHELDON7 115 640021 HALLAM3G 13.8 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.47 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.47 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.48 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.48 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.48 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.48 | P13:NI901T/902T/903T GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.54 | 762779 G18-043 TAP 345 762780 GEN-2018-043 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.54 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.54 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.58 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.58 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.6 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.6 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.67 | P13:SH902T GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.69 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.69 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.69 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.75 | P11:18:SPC: BD #6:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.8 | P11:18:SPC:GPPS#1 GT+SSL - FUT:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.8 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.82 | P11:18:SPC:GPPS#1GT-FUT:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.92 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.11 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.19 | GEN-2021-043_POI_650290_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.28 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.28 | P23:345:XEL:8N17 SHC | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.28 | P23:345:XEL:8N22 SHC | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.29 | 640427 STEELEC9 4.16 640426 STEELEC7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.29 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.29 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.31 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.32 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.33 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.36 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.36 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.41 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.58 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.63 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.73 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.9 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.97 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.97 | Potential P4 Event - POI 659333_5 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.07 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.1 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.1 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.1 | Potential P4 Event - POI 640590_10 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.1 | Potential P4 Event - POI 640590_11 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.11 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.19 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.42 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.46 | Potential P4 Event - POI 645740_12 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 145.01 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 145.11 | GEN-2023-224_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 145.11 | Potential P4 Event - POI 640590_9 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 147.65 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31146 | 141.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31146 | 141.53 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31147 | 141.58 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 141.36 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.35 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.45 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31162 | 141.32 | P12:115:HAST:::LINE | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3123 | 142.27 | P21:161:OPPD:HUMBOLT-S1398:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3123 | 142.28 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31272 | 141.6 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31272 | 141.62 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31548 | 142.77 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31548 | 142.89 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31618 | 142.74 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31618 | 143.64 | P12:115:WERE:KNOB-MKEC-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31618 | 143.66 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.32882 | 154.7 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34901 | 158.38 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34901 | 158.38 | P13:115-161:NPPD:HUMBOLT5:T2::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34901 | 159.72 | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34901 | 160.16 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34901 | 160.18 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.37284 | 175.63 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.55392 | 249.59 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.38615 | 133.36 | GEN-2023-225_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40199 | 132.69 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40238 | 132.68 | Potential P4 Event - POI 640226_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4025 | 132.33 | P23:345:AMMO::MAYWOOD:V33:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40251 | 131.86 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40253 | 133.54 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40254 | 131.98 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40254 | 132.35 | P23:345:MEC:LOUISA 964 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40254 | 132.76 | Potential P4 Event - POI 640226_3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40254 | 133.4 | Potential P4 Event - POI 640226_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 131.81 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 131.82 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 131.82 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 131.83 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 131.89 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 131.92 | 541198 PECULR 7 345 541200 PHILL 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 132.15 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 132.16 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 132.3 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 133.29 | Potential P4 Event - POI 645740_2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 130.75 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.37 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.48 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.48 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.5 | 508563 PIRKEY 7 345 769761 GEN-2022-139 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.51 | 514715 WOODRNG7 345 762321 GEN-2017-164 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.51 | 514787 DEWEY 4 138 766160 GEN-2021-098 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.52 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.52 | 507751 RDPOINT4 138 776581 GEN-2023-230 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.52 | 515543 RENFROW7 345 760809 GEN-2017-203 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.52 | 515802 GRACMNT4 138 774981 GEN-2023-150 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.53 | 514801 MINCO 7 345 761250 GEN-2017-233 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.53 | 523267 PRINGLE 6 230 774441 GEN-2023-123 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.53 | 523309 MOORE_CNTY 6 230 772181 GEN-2023-010 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.53 | 655836 OAKDALE -MK7 115 655853 BEARCREK-MK7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.73 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.73 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.74 | 511560 GRADY 4 138 511567 CHOCTAW4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.75 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.75 | 509829 FULTONW4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.76 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.76 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.76 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.76 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.77 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.79 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.81 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.82 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.83 | P12:138:OKGE:BKRBKR176:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.83 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.88 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.88 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.88 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.89 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.89 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.94 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.94 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.94 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.96 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.96 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.96 | P23:500:EES:PERVIL:R9872 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.96 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.97 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.99 | P41:345:OPPD:S3740-55&CC2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.99 | P42:345:OPPD:S3740-S3455&CC2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.99 | P43:015-345:OPPD:S3740-S3455&CC2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.01 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.01 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.01 | P13:NI901T/902T/903T GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.06 | 762779 G18-043 TAP 345 762780 GEN-2018-043 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.06 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.06 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.09 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.1 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.1 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.12 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.12 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.19 | P13:SH902T GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.2 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.2 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.21 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.27 | P11:18:SPC: BD #6:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.31 | P11:18:SPC:GPPS#1 GT+SSL - FUT:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.31 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.33 | P11:18:SPC:GPPS#1GT-FUT:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.42 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.53 | P23:345:XEL:8P2 KING | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.61 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.68 | GEN-2021-043_POI_650290_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.77 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.77 | P23:345:XEL:8N17 SHC | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.77 | P23:345:XEL:8N22 SHC | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.78 | 640427 STEELEC9 4.16 640426 STEELEC7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.78 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.78 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.8 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.81 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.82 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.85 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.85 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.9 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.06 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.1 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.2 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.36 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.42 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.43 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.43 | Potential P4 Event - POI 659333_5 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.46 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.52 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.55 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.55 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.55 | Potential P4 Event - POI 640590_10 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.55 | Potential P4 Event - POI 640590_11 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.56 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.64 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.86 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.91 | Potential P4 Event - POI 645740_12 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 135.38 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 135.47 | GEN-2023-224_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 135.48 | Potential P4 Event - POI 640590_9 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 137.9 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40257 | 132.05 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40258 | 131.73 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40259 | 132.1 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4026 | 131.89 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.87 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.97 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40279 | 131.85 | P12:115:HAST:::LINE | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40366 | 132.76 | P21:161:OPPD:HUMBOLT-S1398:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40366 | 132.77 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40421 | 132.12 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40421 | 132.14 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40778 | 133.24 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40778 | 133.35 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40868 | 133.21 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40868 | 134.07 | P12:115:WERE:KNOB-MKEC-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40868 | 134.09 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.42502 | 144.66 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45112 | 148.18 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45112 | 149.89 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45112 | 149.9 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.48191 | 164.69 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60871 | 195.57 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60871 | 198.73 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60871 | 198.98 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 771999 G23-222-POI 345 776422 G23-222XFMR1 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 771999 G23-222-POI 345 776425 G23-222XFMR2 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 771999 G23-222-POI 345 776442 G23-223XFMR1 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 776422 G23-222XFMR1 345 776424 G23-222GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 776425 G23-222XFMR2 345 776427 G23-222GEN2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 776442 G23-223XFMR1 345 776444 G23-223GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.29874 | 139.43 | GEN-2023-225_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.311 | 138.72 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31131 | 138.71 | Potential P4 Event - POI 640226_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3114 | 138.33 | P23:345:AMMO::MAYWOOD:V33:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31141 | 137.84 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31142 | 139.62 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31143 | 137.78 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31143 | 137.97 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31143 | 138.36 | P23:345:MEC:LOUISA 964 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31143 | 138.79 | Potential P4 Event - POI 640226_3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31143 | 139.46 | Potential P4 Event - POI 640226_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.49 | 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.49 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.69 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.7 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.71 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.72 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.73 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.73 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.73 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.78 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.79 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.79 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.8 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.8 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.85 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.85 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.86 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.87 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.9 | 541198 PECULR 7 345 541200 PHILL 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.92 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.92 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.94 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.94 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.94 | P23:500:EES:PERVIL:R9872 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.94 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.95 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.96 | P41:345:OPPD:S3740-55&CC2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.96 | P42:345:OPPD:S3740-S3455&CC2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.96 | P45:345:OPPD:S3740-S3455&CC2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 138.07 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 138.15 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 138.15 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 138.3 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 138.55 | P23:345:XEL:8P2 KING | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 139.36 | Potential P4 Event - POI 645740_2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 139.49 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.43 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.43 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.46 | 514715 WOODRNG7 345 762321 GEN-2017-164 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.46 | 514787 DEWEY 4 138 766160 GEN-2021-098 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.47 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.47 | 515802 GRACMNT4 138 774981 GEN-2023-150 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.48 | 514801 MINCO 7 345 761250 GEN-2017-233 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.48 | 515543 RENFROW7 345 760809 GEN-2017-203 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.48 | 523267 PRINGLE 6 230 774441 GEN-2023-123 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.48 | 523309 MOORE_CNTY 6 230 772181 GEN-2023-010 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.49 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.49 | 655840 CHRRYCRK-MK7 115 655876 DPLWCTAP-MK7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.49 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.7 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.71 | 511560 GRADY 4 138 511567 CHOCTAW4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.72 | 509829 FULTONW4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.73 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.76 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.79 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.8 | P12:138:OKGE:BKRBKR176:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.86 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.86 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.92 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.98 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.98 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.99 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.99 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.99 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.99 | P13:NI901T/902T/903T GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.05 | 762779 G18-043 TAP 345 762780 GEN-2018-043 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.05 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.05 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.09 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.09 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.11 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.11 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.18 | P13:SH902T GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.2 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.2 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.21 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.27 | P11:18:SPC: BD #6:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.31 | P11:18:SPC:GPPS#1 GT+SSL - FUT:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.31 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.34 | P11:18:SPC:GPPS#1GT-FUT:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.43 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.64 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.71 | GEN-2021-043_POI_650290_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.8 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.81 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.81 | P23:345:XEL:8N17 SHC | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.81 | P23:345:XEL:8N22 SHC | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.82 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.83 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.84 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.86 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.89 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.89 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.94 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.11 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.16 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.26 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.43 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.5 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.51 | Potential P4 Event - POI 659333_5 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.54 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.61 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.64 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.64 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.64 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.64 | Potential P4 Event - POI 640590_12 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.64 | Potential P4 Event - POI 640590_13 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.72 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.96 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 140.01 | Potential P4 Event - POI 645740_12 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 141.49 | 640112 CLATONA9 34.5 3WXFMR CLATONIA T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 141.58 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 141.68 | GEN-2023-224_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 141.68 | Potential P4 Event - POI 640590_9 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 144.27 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31146 | 137.7 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31146 | 138.04 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31147 | 138.09 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 137.86 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.85 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.96 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31162 | 137.82 | P12:115:HAST:::LINE | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3123 | 138.79 | P21:161:OPPD:HUMBOLT-S1398:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3123 | 138.81 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31272 | 138.11 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31272 | 138.13 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31548 | 139.3 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31548 | 139.42 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31618 | 139.27 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31618 | 140.19 | P12:115:WERE:KNOB-MKEC-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31618 | 140.21 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.32882 | 151.46 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34901 | 155.21 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34901 | 155.21 | P13:115-161:NPPD:HUMBOLT5:T2::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34901 | 156.58 | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34901 | 157.03 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34901 | 157.04 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.37284 | 172.8 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.55392 | 248.32 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 771999 G23-222-POI 345 776422 G23-222XFMR1 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 771999 G23-222-POI 345 776425 G23-222XFMR2 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 771999 G23-222-POI 345 776442 G23-223XFMR1 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 776422 G23-222XFMR1 345 776424 G23-222GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 776425 G23-222XFMR2 345 776427 G23-222GEN2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 776442 G23-223XFMR1 345 776444 G23-223GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | 193 | 193 | 0.27226 | 139.25 | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 193 | 193 | 0.22818 | 101.08 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 193 | 193 | 0.27341 | 139.83 | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.2343 | 175.6 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.2343 | 177.52 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.2343 | 177.77 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.26662 | 198.16 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.29874 | 142.9 | GEN-2023-225_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.311 | 142.19 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31131 | 142.19 | Potential P4 Event - POI 640226_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3114 | 141.82 | P23:345:AMMO::MAYWOOD:V33:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31141 | 141.33 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31142 | 143.08 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31143 | 141.27 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31143 | 141.46 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31143 | 141.84 | P23:345:MEC:LOUISA 964 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31143 | 142.27 | Potential P4 Event - POI 640226_3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31143 | 142.94 | Potential P4 Event - POI 640226_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 140.99 | 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 140.99 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.19 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.19 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.21 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.22 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.22 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.23 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.23 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.28 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.28 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.29 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.3 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.3 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.35 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.35 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.36 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.36 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.39 | 541198 PECULR 7 345 541200 PHILL 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.42 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.42 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.43 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.43 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.43 | P23:500:EES:PERVIL:R9872 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.43 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.44 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.47 | P41:345:OPPD:S3740-55&CC2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.47 | P42:345:OPPD:S3740-S3455&CC2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.47 | P43:015-345:OPPD:S3740-S3455&CC2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.57 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.64 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.64 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.79 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 142.03 | P23:345:XEL:8P2 KING | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 142.83 | Potential P4 Event - POI 645740_2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 142.96 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.93 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.94 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.96 | 514715 WOODRNG7 345 762321 GEN-2017-164 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.96 | 514787 DEWEY 4 138 766160 GEN-2021-098 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.97 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.97 | 515802 GRACMNT4 138 774981 GEN-2023-150 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.98 | 514801 MINCO 7 345 761250 GEN-2017-233 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.98 | 515543 RENFROW7 345 760809 GEN-2017-203 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.98 | 523267 PRINGLE 6 230 774441 GEN-2023-123 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.98 | 523309 MOORE_CNTY 6 230 772181 GEN-2023-010 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.99 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.99 | 655840 CHRRYCRK-MK7 115 655876 DPLWCTAP-MK7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.99 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.2 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.21 | 509829 FULTONW4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.21 | 511560 GRADY 4 138 511567 CHOCTAW4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.22 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.25 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.29 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.3 | P12:138:OKGE:BKRBKR176:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.35 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.36 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.42 | 640278 SHELDON7 115 640021 HALLAM3G 13.8 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.47 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.47 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.48 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.48 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.48 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.48 | P13:NI901T/902T/903T GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.54 | 762779 G18-043 TAP 345 762780 GEN-2018-043 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.54 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.54 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.58 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.58 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.6 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.6 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.67 | P13:SH902T GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.69 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.69 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.69 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.75 | P11:18:SPC: BD #6:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.8 | P11:18:SPC:GPPS#1 GT+SSL - FUT:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.8 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.82 | P11:18:SPC:GPPS#1GT-FUT:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.92 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.11 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.19 | GEN-2021-043_POI_650290_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.28 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.28 | P23:345:XEL:8N17 SHC | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.28 | P23:345:XEL:8N22 SHC | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.29 | 640427 STEELEC9 4.16 640426 STEELEC7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.29 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.29 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.31 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.32 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.33 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.36 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.36 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.41 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.58 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.63 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.73 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.9 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.97 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.97 | Potential P4 Event - POI 659333_5 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.07 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.1 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.1 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.1 | Potential P4 Event - POI 640590_10 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.1 | Potential P4 Event - POI 640590_11 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.11 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.19 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.42 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.46 | Potential P4 Event - POI 645740_12 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 145.01 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 145.11 | GEN-2023-224_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 145.11 | Potential P4 Event - POI 640590_9 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 147.65 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31146 | 141.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31146 | 141.53 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31147 | 141.58 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 141.36 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.35 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.45 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31162 | 141.32 | P12:115:HAST:::LINE | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3123 | 142.27 | P21:161:OPPD:HUMBOLT-S1398:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3123 | 142.28 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31272 | 141.6 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31272 | 141.62 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31548 | 142.77 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31548 | 142.89 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31618 | 142.74 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31618 | 143.64 | P12:115:WERE:KNOB-MKEC-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31618 | 143.66 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.32882 | 154.7 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34901 | 158.38 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34901 | 158.38 | P13:115-161:NPPD:HUMBOLT5:T2::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34901 | 159.72 | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34901 | 160.16 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34901 | 160.18 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.37284 | 175.63 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.55392 | 249.59 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.38615 | 133.36 | GEN-2023-225_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40199 | 132.69 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40238 | 132.68 | Potential P4 Event - POI 640226_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4025 | 132.33 | P23:345:AMMO::MAYWOOD:V33:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40251 | 131.86 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40253 | 133.54 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40254 | 131.98 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40254 | 132.35 | P23:345:MEC:LOUISA 964 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40254 | 132.76 | Potential P4 Event - POI 640226_3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40254 | 133.4 | Potential P4 Event - POI 640226_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 131.81 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 131.82 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 131.82 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 131.83 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 131.89 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 131.92 | 541198 PECULR 7 345 541200 PHILL 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 132.15 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 132.16 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 132.3 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 133.29 | Potential P4 Event - POI 645740_2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 130.75 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.37 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.48 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.48 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.5 | 508563 PIRKEY 7 345 769761 GEN-2022-139 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.51 | 514715 WOODRNG7 345 762321 GEN-2017-164 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.51 | 514787 DEWEY 4 138 766160 GEN-2021-098 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.52 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.52 | 507751 RDPOINT4 138 776581 GEN-2023-230 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.52 | 515543 RENFROW7 345 760809 GEN-2017-203 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.52 | 515802 GRACMNT4 138 774981 GEN-2023-150 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.53 | 514801 MINCO 7 345 761250 GEN-2017-233 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.53 | 523267 PRINGLE 6 230 774441 GEN-2023-123 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.53 | 523309 MOORE_CNTY 6 230 772181 GEN-2023-010 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.53 | 655836 OAKDALE -MK7 115 655853 BEARCREK-MK7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.73 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.73 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.74 | 511560 GRADY 4 138 511567 CHOCTAW4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.75 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.75 | 509829 FULTONW4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.76 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.76 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.76 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.76 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.77 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.79 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.81 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.82 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.83 | P12:138:OKGE:BKRBKR176:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.83 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.88 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.88 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.88 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.89 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.89 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.94 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.94 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.94 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.96 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.96 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.96 | P23:500:EES:PERVIL:R9872 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.96 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.97 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.99 | P41:345:OPPD:S3740-55&CC2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.99 | P42:345:OPPD:S3740-S3455&CC2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.99 | P43:015-345:OPPD:S3740-S3455&CC2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.01 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.01 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.01 | P13:NI901T/902T/903T GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.06 | 762779 G18-043 TAP 345 762780 GEN-2018-043 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.06 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.06 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.09 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.1 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.1 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.12 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.12 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.19 | P13:SH902T GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.2 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.2 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.21 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.27 | P11:18:SPC: BD #6:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.31 | P11:18:SPC:GPPS#1 GT+SSL - FUT:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.31 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.33 | P11:18:SPC:GPPS#1GT-FUT:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.42 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.53 | P23:345:XEL:8P2 KING | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.61 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.68 | GEN-2021-043_POI_650290_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.77 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.77 | P23:345:XEL:8N17 SHC | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.77 | P23:345:XEL:8N22 SHC | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.78 | 640427 STEELEC9 4.16 640426 STEELEC7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.78 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.78 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.8 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.81 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.82 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.85 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.85 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.9 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.06 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.1 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.2 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.36 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.42 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.43 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.43 | Potential P4 Event - POI 659333_5 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.46 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.52 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.55 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.55 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.55 | Potential P4 Event - POI 640590_10 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.55 | Potential P4 Event - POI 640590_11 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.56 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.64 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.86 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.91 | Potential P4 Event - POI 645740_12 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 135.38 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 135.47 | GEN-2023-224_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 135.48 | Potential P4 Event - POI 640590_9 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 137.9 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40257 | 132.05 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40258 | 131.73 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40259 | 132.1 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4026 | 131.89 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.87 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.97 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40279 | 131.85 | P12:115:HAST:::LINE | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40366 | 132.76 | P21:161:OPPD:HUMBOLT-S1398:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40366 | 132.77 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40421 | 132.12 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40421 | 132.14 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40778 | 133.24 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40778 | 133.35 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40868 | 133.21 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40868 | 134.07 | P12:115:WERE:KNOB-MKEC-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40868 | 134.09 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.42502 | 144.66 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45112 | 148.18 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45112 | 149.89 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45112 | 149.9 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.48191 | 164.69 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60871 | 195.57 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60871 | 198.73 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60871 | 198.98 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 771999 G23-222-POI 345 776422 G23-222XFMR1 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 771999 G23-222-POI 345 776425 G23-222XFMR2 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 776422 G23-222XFMR1 345 776424 G23-222GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 776425 G23-222XFMR2 345 776427 G23-222GEN2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.29874 | 139.43 | GEN-2023-225_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.311 | 138.72 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31131 | 138.71 | Potential P4 Event - POI 640226_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3114 | 138.33 | P23:345:AMMO::MAYWOOD:V33:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31141 | 137.84 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31142 | 139.62 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31143 | 137.78 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31143 | 137.97 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31143 | 138.36 | P23:345:MEC:LOUISA 964 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31143 | 138.79 | Potential P4 Event - POI 640226_3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31143 | 139.46 | Potential P4 Event - POI 640226_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.49 | 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.49 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.69 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.7 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.71 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.72 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.73 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.73 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.73 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.78 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.79 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.79 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.8 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.8 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.85 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.85 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.86 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.87 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.9 | 541198 PECULR 7 345 541200 PHILL 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.92 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.92 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.94 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.94 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.94 | P23:500:EES:PERVIL:R9872 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.94 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.95 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.96 | P41:345:OPPD:S3740-55&CC2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.96 | P42:345:OPPD:S3740-S3455&CC2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.96 | P45:345:OPPD:S3740-S3455&CC2:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 138.07 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 138.15 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 138.15 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 138.3 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 138.55 | P23:345:XEL:8P2 KING | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 139.36 | Potential P4 Event - POI 645740_2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 139.49 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.43 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.43 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.46 | 514715 WOODRNG7 345 762321 GEN-2017-164 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.46 | 514787 DEWEY 4 138 766160 GEN-2021-098 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.47 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.47 | 515802 GRACMNT4 138 774981 GEN-2023-150 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.48 | 514801 MINCO 7 345 761250 GEN-2017-233 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.48 | 515543 RENFROW7 345 760809 GEN-2017-203 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.48 | 523267 PRINGLE 6 230 774441 GEN-2023-123 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.48 | 523309 MOORE_CNTY 6 230 772181 GEN-2023-010 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.49 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.49 | 655840 CHRRYCRK-MK7 115 655876 DPLWCTAP-MK7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.49 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.7 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.71 | 511560 GRADY 4 138 511567 CHOCTAW4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.72 | 509829 FULTONW4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.73 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.76 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.79 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.8 | P12:138:OKGE:BKRBKR176:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.86 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.86 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.92 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.98 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.98 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.99 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.99 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.99 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.99 | P13:NI901T/902T/903T GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.05 | 762779 G18-043 TAP 345 762780 GEN-2018-043 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.05 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.05 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.09 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.09 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.11 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.11 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.18 | P13:SH902T GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.2 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.2 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.21 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.27 | P11:18:SPC: BD #6:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.31 | P11:18:SPC:GPPS#1 GT+SSL - FUT:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.31 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.34 | P11:18:SPC:GPPS#1GT-FUT:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.43 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.64 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.71 | GEN-2021-043_POI_650290_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.8 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.81 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.81 | P23:345:XEL:8N17 SHC | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.81 | P23:345:XEL:8N22 SHC | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.82 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.83 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.84 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.86 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.89 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.89 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.94 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.11 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.16 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.26 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.43 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.5 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.51 | Potential P4 Event - POI 659333_5 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.54 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.61 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.64 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.64 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.64 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.64 | Potential P4 Event - POI 640590_12 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.64 | Potential P4 Event - POI 640590_13 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.72 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.96 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 140.01 | Potential P4 Event - POI 645740_12 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 141.49 | 640112 CLATONA9 34.5 3WXFMR CLATONIA T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 141.58 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 141.68 | GEN-2023-224_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 141.68 | Potential P4 Event - POI 640590_9 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 144.27 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31146 | 137.7 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31146 | 138.04 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31147 | 138.09 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 137.86 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.85 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.96 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31162 | 137.82 | P12:115:HAST:::LINE | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3123 | 138.79 | P21:161:OPPD:HUMBOLT-S1398:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3123 | 138.81 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31272 | 138.11 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31272 | 138.13 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31548 | 139.3 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31548 | 139.42 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31618 | 139.27 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31618 | 140.19 | P12:115:WERE:KNOB-MKEC-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31618 | 140.21 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.32882 | 151.46 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34901 | 155.21 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34901 | 155.21 | P13:115-161:NPPD:HUMBOLT5:T2::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34901 | 156.58 | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34901 | 157.03 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34901 | 157.04 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.37284 | 172.8 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.55392 | 248.32 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 771999 G23-222-POI 345 776422 G23-222XFMR1 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 771999 G23-222-POI 345 776425 G23-222XFMR2 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 776422 G23-222XFMR1 345 776424 G23-222GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 776425 G23-222XFMR2 345 776427 G23-222GEN2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.5901 | 101.17 | 509050 KEATCHI4 138 509052 STONWAL4 138 1 | TDF Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.5901 | 102.22 | 507793 LEASIDE 4 138 509052 STONWAL4 138 1 | TDF Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.60098 | 103.99 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.60098 | 103.99 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.60098 | 103.99 | Potential P4 Event - POI 508359_5 | TDF Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 1 | 123.27 | Potential P4 Event - POI 645740_1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-077 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 1 | 137.37 | Potential P4 Event - POI 645740_0 | TDF Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 1 | 123.27 | Potential P4 Event - POI 645740_1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-078 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 1 | 137.37 | Potential P4 Event - POI 645740_0 | TDF Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 1 | 123.27 | Potential P4 Event - POI 645740_1 | TDF Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-079 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 1 | 137.37 | Potential P4 Event - POI 645740_0 | TDF Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | 193 | 193 | 0.27292 | 137.22 | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 193 | 193 | 0.22846 | 100.54 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 193 | 193 | 0.27408 | 137.79 | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.20001 | 143.13 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.20001 | 144.87 | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.20001 | 145.42 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.2342 | 162.09 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.2342 | 163.84 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.2342 | 164.05 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.26649 | 183.26 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.29854 | 136.05 | GEN-2023-225_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31064 | 134.96 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31099 | 135.29 | Potential P4 Event - POI 640226_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31102 | 134.53 | P45:345:OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31107 | 134.63 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31109 | 134.66 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31111 | 134.8 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31111 | 135.93 | Potential P4 Event - POI 640226_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31111 | 136.15 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31112 | 134.69 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31113 | 134.46 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31113 | 134.48 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31113 | 134.49 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31113 | 134.97 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31113 | 134.97 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31113 | 135.14 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31113 | 135.45 | Potential P4 Event - POI 640226_3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31113 | 135.88 | Potential P4 Event - POI 645740_2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.03 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.19 | 514823 ROMNOSE4 138 775201 GEN-2023-161 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.19 | 515150 CANEYCK4 138 769841 GEN-2022-143 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.2 | 520893 EL RENO4 138 588720 GEN-2017-117 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.21 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.21 | 514787 DEWEY 4 138 766160 GEN-2021-098 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.21 | 520860 COLBERT4 138 769701 GEN-2022-136 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.22 | 515055 MAUD 4 138 771742 G22-238XFMR1 34.5 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.23 | 301643 FOXTROTGSU 34.5 3WXFMR FOXTROTGSU 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.23 | 523823 CARPENTER 7 345 764980 GEN-2020-008 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.23 | 526936 YOAKUM 7 345 766120 GEN-2021-090 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.23 | 655840 CHRRYCRK-MK7 115 655876 DPLWCTAP-MK7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.23 | 655846 F9______-MK7 115 655888 BANKS -MK7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.23 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.23 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.24 | 345831 4TAUM S 1 138 345832 1TAUM S G1 13.8 G1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.24 | 508359 WELSH 7 345 765660 GEN-2021-038 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.24 | 523267 PRINGLE 6 230 774441 GEN-2023-123 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.24 | 523309 MOORE_CNTY 6 230 772181 GEN-2023-010 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.24 | 655882 GALAXYTP-MK7 115 655884 DEMCKSLK-MK7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.44 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.44 | 512650 GRDA1 7 345 774740 G23-138-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.45 | 511560 GRADY 4 138 511567 CHOCTAW4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.45 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.46 | P12:HV:EES::4SCOTT_1!:4BLOOMFLD%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.47 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.47 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.47 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.49 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.53 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.53 | P12:161:OKGE:BKRBKR197:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.57 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.57 | P12:161:AEPW-SWPA:BEAVER5:EROGERS5::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.57 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.57 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.58 | P12:HV:EES::6DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.59 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.59 | P21:161:ALTW:AUTO-SINGLE:CRYSTLK5:CLKREACT5:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.59 | P21:161:ALTW:AUTO-SINGLE:LIMECKL15:CLKREACT5:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.59 | P23:500:EES:PERVIL:R9872 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.59 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.59 | P23:500:EMI:ABF_PRYVL-B | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.6 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.6 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.61 | P12:161:AEPW:DYESS5:ELMSPRNG:TONTITN5:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.61 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.61 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.62 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.62 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.64 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.67 | 640119 COL.COG7 115 640028 COLCOG1G 13.8 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.69 | 51993 J2199 SUB 345 3WXFMR J2199 SUB 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.74 | P13:230:UMZW:# 5137 #:: OA IN SD. FAULT ON TRANSFORMER (4).:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.75 | 620322 BSSOUTH4 230 621317 CROWN CAP 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.75 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.77 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.79 | P13:RU901T | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.82 | P13:PR901T GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.82 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.84 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.85 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.85 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.86 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.86 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.88 | P21:345:XEL:AUTO-SINGLE:WILMART3:MEC-345:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.9 | P23:345:OTP::TWIN BRKS 3:BRKY_V2021:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.91 | P11:18:SPC:PR#1:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.95 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.99 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.99 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.14 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.26 | P23:345:XEL:8P2 KING | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.27 | P11:18:SPC: BD #6+SSL:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.31 | 645740 S3740 3 345 773564 G23-079GEN1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.31 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.35 | P11:18:SPC: BD #6:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.43 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.47 | GEN-2021-043_POI_650290_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.48 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.5 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.5 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.5 | P23:345:XEL:8N17 SHC | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.5 | P23:345:XEL:8N22 SHC | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.52 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.54 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.55 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.58 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.58 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.71 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.84 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.93 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.04 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.05 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.06 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.07 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.13 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.17 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.22 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.22 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.22 | Potential P4 Event - POI 640590_11 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.22 | Potential P4 Event - POI 640590_13 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.28 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.3 | Potential P4 Event - POI 659333_5 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.5 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.52 | Potential P4 Event - POI 645740_12 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.9 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 138.13 | GEN-2023-224_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 138.13 | Potential P4 Event - POI 640590_9 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 141.62 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31115 | 134.61 | 542980 NASHUA 7 345 542982 IATAN 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31115 | 134.75 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31116 | 134.67 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31117 | 134.57 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31118 | 134.83 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31119 | 134.58 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31203 | 135.9 | P21:161:OPPD:HUMBOLT-S1398:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31203 | 135.91 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31247 | 135.01 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31247 | 135.12 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31523 | 136.4 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31523 | 136.49 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31597 | 136.54 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31597 | 137.27 | P12:115:WERE:KNOB-MKEC-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31597 | 137.29 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.32881 | 148.17 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34895 | 153.08 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34895 | 153.08 | P13:115-161:NPPD:HUMBOLT5:T2::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34895 | 154.9 | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34895 | 155.51 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34895 | 155.52 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.37252 | 166.49 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.55338 | 242.37 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.38588 | 127.16 | GEN-2023-225_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40152 | 126.11 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40197 | 126.43 | Potential P4 Event - POI 640226_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40208 | 125.8 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4021 | 125.83 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40213 | 125.97 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40213 | 127.04 | Potential P4 Event - POI 640226_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40213 | 127.26 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40214 | 125.86 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40215 | 125.65 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40215 | 126.58 | Potential P4 Event - POI 640226_3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.64 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.65 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.67 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.74 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.76 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.76 | P23:500:EES:PERVIL:R9872 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.76 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.76 | P23:500:EMI:ABF_PRYVL-B | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.77 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.79 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.79 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 126.12 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 126.13 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 126.28 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 126.99 | Potential P4 Event - POI 645740_2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.23 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.36 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.36 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.37 | 509895 T.NO.2-4 138 762636 GEN-2018-028 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.38 | 508286 CAMPCOR4 138 765980 GEN-2021-075 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.38 | 508563 PIRKEY 7 345 769761 GEN-2022-139 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.38 | 514823 ROMNOSE4 138 775201 GEN-2023-161 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.38 | 515150 CANEYCK4 138 769841 GEN-2022-143 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.38 | 525830 TUCO_INT 6 230 525840 ANTELOPE_1 6 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.38 | 526299 LUBBCK_EST 6 230 764875 GEN-2020-060 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.39 | 520893 EL RENO4 138 588720 GEN-2017-117 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.4 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.4 | 514787 DEWEY 4 138 766160 GEN-2021-098 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.4 | 520860 COLBERT4 138 769701 GEN-2022-136 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.4 | 655882 GALAXYTP-MK7 115 659388 KUMMERDG-MK7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.41 | 515055 MAUD 4 138 771742 G22-238XFMR1 34.5 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.41 | 655846 F9______-MK7 115 655872 G9TAP___-MK7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.42 | 523823 CARPENTER 7 345 764980 GEN-2020-008 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.42 | 525481 PLANT_X 6 230 775501 GEN-2023-176 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.42 | 655836 OAKDALE -MK7 115 655853 BEARCREK-MK7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.42 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.42 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.62 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.63 | 511560 GRADY 4 138 511567 CHOCTAW4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.64 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.64 | P12:HV:EES::4SCOTT_1!:4BLOOMFLD%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.65 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.67 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.7 | P12:161:AEPW:EROGERS5:ECNTRTN5::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.7 | P12:161:OKGE:BKRBKR197:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.71 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.74 | P12:161:AEPW-SWPA:BEAVER5:EROGERS5::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.74 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.75 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.75 | P12:HV:EES::6DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.76 | P21:161:ALTW:AUTO-SINGLE:CRYSTLK5:CLKREACT5:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.76 | P21:161:ALTW:AUTO-SINGLE:LIMECKL15:CLKREACT5:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.77 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.78 | P12:161:AEPW:DYESS5:ELMSPRNG:TONTITN5:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.78 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.78 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.81 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.84 | 640119 COL.COG7 115 640028 COLCOG1G 13.8 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.85 | 51993 J2199 SUB 345 3WXFMR J2199 SUB 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.9 | P13:230:UMZW:# 5137 #:: OA IN SD. FAULT ON TRANSFORMER (4).:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.92 | 620322 BSSOUTH4 230 621317 CROWN CAP 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.92 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.93 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.95 | P13:RU901T | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.98 | P13:PR901T GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.98 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.01 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.01 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.02 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.02 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.04 | P21:345:XEL:AUTO-SINGLE:WILMART3:MEC-345:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.06 | P23:345:OTP::TWIN BRKS 3:BRKY_V2021:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.11 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.15 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.15 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.29 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.4 | P23:345:XEL:8P2 KING | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.45 | 645740 S3740 3 345 773564 G23-079GEN1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.45 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.6 | GEN-2021-043_POI_650290_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.61 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.63 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.63 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.63 | P23:345:XEL:8N17 SHC | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.63 | P23:345:XEL:8N22 SHC | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.65 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.67 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.83 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.95 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.04 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.15 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.16 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.17 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.18 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.23 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.27 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.32 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.32 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.32 | Potential P4 Event - POI 640590_11 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.32 | Potential P4 Event - POI 640590_13 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.38 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.39 | Potential P4 Event - POI 659333_5 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.59 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.61 | Potential P4 Event - POI 645740_12 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.97 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 129.14 | GEN-2023-224_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 129.15 | Potential P4 Event - POI 640590_9 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 132.48 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40218 | 125.78 | 542980 NASHUA 7 345 542982 IATAN 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40219 | 125.84 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40219 | 125.92 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4022 | 125.74 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40222 | 125.99 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40223 | 125.75 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40332 | 127.02 | P21:161:OPPD:HUMBOLT-S1398:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40332 | 127.03 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40388 | 126.16 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40388 | 126.27 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40746 | 127.49 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40746 | 127.58 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40841 | 127.63 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40841 | 128.33 | P12:115:WERE:KNOB-MKEC-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40841 | 128.34 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.42501 | 138.75 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45104 | 143.46 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45104 | 145.8 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45104 | 145.81 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4815 | 156.31 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60812 | 189.98 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60812 | 192.94 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60812 | 193.15 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.4 | 771999 G23-222-POI 345 776422 G23-222XFMR1 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.4 | 771999 G23-222-POI 345 776425 G23-222XFMR2 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.4 | 771999 G23-222-POI 345 776442 G23-223XFMR1 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.4 | 776422 G23-222XFMR1 345 776424 G23-222GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.4 | 776425 G23-222XFMR2 345 776427 G23-222GEN2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.4 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.14 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.54 | 772201 GEN-2023-011 115 772202 G23-011XFMR1 34.5 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.54 | GEN-2023-011_POI_640208_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.59 | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.6 | 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.61 | 640208 HARBINE7 115 640426 STEELEC7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.61 | Potential P4 Event - POI 640590_3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.62 | Potential P4 Event - POI 640590_7 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.62 | Potential P4 Event - POI 640590_8 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.63 | P13:115-345:NPPD:MONOLITH 3:T1::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.63 | P13:115-345:NPPD:MONOLITH 3:T2::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.63 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.63 | Potential P4 Event - POI 640525_3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.63 | Potential P4 Event - POI 640525_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.63 | Potential P4 Event - POI 640525_5 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.63 | Potential P4 Event - POI 645740_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.29854 | 133.06 | GEN-2023-225_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31064 | 131.95 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31099 | 132.29 | Potential P4 Event - POI 640226_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31107 | 131.62 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31109 | 131.65 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31111 | 131.79 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31111 | 132.93 | Potential P4 Event - POI 640226_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31111 | 133.16 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31112 | 131.68 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31113 | 131.44 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31113 | 131.46 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31113 | 131.48 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31113 | 131.96 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31113 | 131.96 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31113 | 132.13 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31113 | 132.45 | Potential P4 Event - POI 640226_3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31113 | 132.89 | Potential P4 Event - POI 645740_2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.01 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.17 | 514823 ROMNOSE4 138 775201 GEN-2023-161 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.17 | 515150 CANEYCK4 138 769841 GEN-2022-143 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.18 | 520893 EL RENO4 138 588720 GEN-2017-117 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.19 | 514787 DEWEY 4 138 766160 GEN-2021-098 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.19 | 520860 COLBERT4 138 769701 GEN-2022-136 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.21 | 301643 FOXTROTGSU 34.5 3WXFMR FOXTROTGSU 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.21 | 523267 PRINGLE 6 230 774441 GEN-2023-123 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.21 | 523309 MOORE_CNTY 6 230 772181 GEN-2023-010 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.21 | 523823 CARPENTER 7 345 764980 GEN-2020-008 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.21 | 526936 YOAKUM 7 345 766120 GEN-2021-090 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.21 | 655840 CHRRYCRK-MK7 115 655876 DPLWCTAP-MK7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.21 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.21 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.22 | 345831 4TAUM S 1 138 345832 1TAUM S G1 13.8 G1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.22 | 345840 4TAUM S 2 138 345841 1TAUM S G2 13.8 G2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.22 | 508359 WELSH 7 345 765660 GEN-2021-038 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.22 | 532772 STRANGR7 345 3WXFMR STRANGR TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.22 | 655876 DPLWCTAP-MK7 115 655877 LITTLMS4-MK7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.22 | 655882 GALAXYTP-MK7 115 655884 DEMCKSLK-MK7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.42 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.42 | 512650 GRDA1 7 345 774740 G23-138-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.43 | 511560 GRADY 4 138 511567 CHOCTAW4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.43 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.44 | P12:HV:EES::4SCOTT_1!:4BLOOMFLD%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.45 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.46 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.46 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.48 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.51 | P12:161:AEPW:EROGERS5:ECNTRTN5::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.52 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.52 | P12:161:OKGE:BKRBKR197:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.56 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.56 | P12:161:AEPW-SWPA:BEAVER5:EROGERS5::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.56 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.56 | P12:HV:EES::6DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.56 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.58 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.58 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.58 | P21:161:ALTW:AUTO-SINGLE:CRYSTLK5:CLKREACT5:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.58 | P21:161:ALTW:AUTO-SINGLE:LIMECKL15:CLKREACT5:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.58 | P23:500:EES:PERVIL:R9872 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.58 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.59 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.59 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.6 | P12:161:AEPW:DYESS5:ELMSPRNG:TONTITN5:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.6 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.6 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.6 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.6 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.62 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.65 | 640119 COL.COG7 115 640028 COLCOG1G 13.8 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.67 | 51993 J2199 SUB 345 3WXFMR J2199 SUB 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.73 | P13:230:UMZW:# 5137 #:: OA IN SD. FAULT ON TRANSFORMER (4).:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.74 | 620322 BSSOUTH4 230 621317 CROWN CAP 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.74 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.76 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.78 | P13:RU901T | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.81 | P13:PR901T GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.81 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.83 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.84 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.84 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.85 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.85 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.87 | P21:345:XEL:AUTO-SINGLE:WILMART3:MEC-345:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.89 | P23:345:OTP::TWIN BRKS 3:BRKY_V2021:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.9 | P11:18:SPC:PR#1:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.95 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.98 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.99 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.14 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.25 | P23:345:XEL:8P2 KING | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.27 | P11:18:SPC: BD #6+SSL:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.31 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.35 | P11:18:SPC: BD #6:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.43 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.47 | GEN-2021-043_POI_650290_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.48 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.5 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.5 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.5 | P23:345:XEL:8N17 SHC | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.5 | P23:345:XEL:8N22 SHC | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.52 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.54 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.55 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.58 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.58 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.71 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.84 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.94 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.05 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.07 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.07 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.08 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.14 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.18 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.24 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.24 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.24 | Potential P4 Event - POI 640590_10 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.24 | Potential P4 Event - POI 640590_12 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.3 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.31 | Potential P4 Event - POI 659333_5 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.52 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.54 | Potential P4 Event - POI 645740_12 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.93 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 134.78 | 640112 CLATONA9 34.5 3WXFMR CLATONIA T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 135.18 | GEN-2023-224_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 135.18 | Potential P4 Event - POI 640590_9 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 138.74 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31115 | 131.6 | 542980 NASHUA 7 345 542982 IATAN 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31115 | 131.74 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31116 | 131.66 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31117 | 131.55 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31118 | 131.82 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31119 | 131.57 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31203 | 132.92 | P21:161:OPPD:HUMBOLT-S1398:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31203 | 132.93 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31247 | 132 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31247 | 132.12 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31523 | 133.41 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31523 | 133.51 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31597 | 133.56 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31597 | 134.31 | P12:115:WERE:KNOB-MKEC-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31597 | 134.32 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.32881 | 145.41 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34895 | 150.44 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34895 | 150.44 | P13:115-161:NPPD:HUMBOLT5:T2::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34895 | 152.31 | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34895 | 152.93 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34895 | 152.94 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.37252 | 164.13 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.55338 | 241.55 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.04 | 771999 G23-222-POI 345 776422 G23-222XFMR1 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.04 | 771999 G23-222-POI 345 776425 G23-222XFMR2 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.04 | 771999 G23-222-POI 345 776442 G23-223XFMR1 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.04 | 776422 G23-222XFMR1 345 776424 G23-222GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.04 | 776425 G23-222XFMR2 345 776427 G23-222GEN2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.04 | 776442 G23-223XFMR1 345 776444 G23-223GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.04 | GEN-2023-223_POI_771999_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 171.1 | Potential P4 Event - POI 640590_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 171.12 | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 171.12 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 171.13 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 171.41 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 171.44 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 171.44 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 171.47 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | 193 | 193 | 0.27292 | 137.22 | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 193 | 193 | 0.22846 | 100.54 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 193 | 193 | 0.27408 | 137.79 | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.20001 | 143.13 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.20001 | 144.87 | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.20001 | 145.42 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.2342 | 162.09 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.2342 | 163.84 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.2342 | 164.05 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.26649 | 183.26 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.29854 | 136.05 | GEN-2023-225_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31064 | 134.96 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31099 | 135.29 | Potential P4 Event - POI 640226_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31102 | 134.53 | P45:345:OPPD:S3456-S3458&CBL:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31107 | 134.63 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31109 | 134.66 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31111 | 134.8 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31111 | 135.93 | Potential P4 Event - POI 640226_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31111 | 136.15 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31112 | 134.69 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31113 | 134.46 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31113 | 134.48 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31113 | 134.49 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31113 | 134.97 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31113 | 134.97 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31113 | 135.14 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31113 | 135.45 | Potential P4 Event - POI 640226_3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31113 | 135.88 | Potential P4 Event - POI 645740_2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.03 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.19 | 514823 ROMNOSE4 138 775201 GEN-2023-161 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.19 | 515150 CANEYCK4 138 769841 GEN-2022-143 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.2 | 520893 EL RENO4 138 588720 GEN-2017-117 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.21 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.21 | 514787 DEWEY 4 138 766160 GEN-2021-098 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.21 | 520860 COLBERT4 138 769701 GEN-2022-136 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.22 | 515055 MAUD 4 138 771742 G22-238XFMR1 34.5 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.23 | 301643 FOXTROTGSU 34.5 3WXFMR FOXTROTGSU 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.23 | 523823 CARPENTER 7 345 764980 GEN-2020-008 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.23 | 526936 YOAKUM 7 345 766120 GEN-2021-090 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.23 | 655840 CHRRYCRK-MK7 115 655876 DPLWCTAP-MK7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.23 | 655846 F9______-MK7 115 655888 BANKS -MK7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.23 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.23 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.24 | 345831 4TAUM S 1 138 345832 1TAUM S G1 13.8 G1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.24 | 508359 WELSH 7 345 765660 GEN-2021-038 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.24 | 523267 PRINGLE 6 230 774441 GEN-2023-123 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.24 | 523309 MOORE_CNTY 6 230 772181 GEN-2023-010 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.24 | 655882 GALAXYTP-MK7 115 655884 DEMCKSLK-MK7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.44 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.44 | 512650 GRDA1 7 345 774740 G23-138-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.45 | 511560 GRADY 4 138 511567 CHOCTAW4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.45 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.46 | P12:HV:EES::4SCOTT_1!:4BLOOMFLD%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.47 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.47 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.47 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.49 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.53 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.53 | P12:161:OKGE:BKRBKR197:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.57 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.57 | P12:161:AEPW-SWPA:BEAVER5:EROGERS5::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.57 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.57 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.58 | P12:HV:EES::6DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.59 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.59 | P21:161:ALTW:AUTO-SINGLE:CRYSTLK5:CLKREACT5:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.59 | P21:161:ALTW:AUTO-SINGLE:LIMECKL15:CLKREACT5:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.59 | P23:500:EES:PERVIL:R9872 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.59 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.59 | P23:500:EMI:ABF_PRYVL-B | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.6 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.6 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.61 | P12:161:AEPW:DYESS5:ELMSPRNG:TONTITN5:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.61 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.61 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.62 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.62 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.64 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.67 | 640119 COL.COG7 115 640028 COLCOG1G 13.8 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.69 | 51993 J2199 SUB 345 3WXFMR J2199 SUB 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.74 | P13:230:UMZW:# 5137 #:: OA IN SD. FAULT ON TRANSFORMER (4).:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.75 | 620322 BSSOUTH4 230 621317 CROWN CAP 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.75 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.77 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.79 | P13:RU901T | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.82 | P13:PR901T GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.82 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.84 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.85 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.85 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.86 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.86 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.88 | P21:345:XEL:AUTO-SINGLE:WILMART3:MEC-345:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.9 | P23:345:OTP::TWIN BRKS 3:BRKY_V2021:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.91 | P11:18:SPC:PR#1:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.95 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.99 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.99 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.14 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.26 | P23:345:XEL:8P2 KING | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.27 | P11:18:SPC: BD #6+SSL:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.31 | 645740 S3740 3 345 773564 G23-079GEN1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.31 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.35 | P11:18:SPC: BD #6:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.43 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.47 | GEN-2021-043_POI_650290_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.48 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.5 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.5 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.5 | P23:345:XEL:8N17 SHC | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.5 | P23:345:XEL:8N22 SHC | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.52 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.54 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.55 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.58 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.58 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.71 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.84 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.93 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.04 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.05 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.06 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.07 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.13 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.17 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.22 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.22 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.22 | Potential P4 Event - POI 640590_11 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.22 | Potential P4 Event - POI 640590_13 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.28 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.3 | Potential P4 Event - POI 659333_5 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.5 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.52 | Potential P4 Event - POI 645740_12 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.9 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 138.13 | GEN-2023-224_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 138.13 | Potential P4 Event - POI 640590_9 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 141.62 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31115 | 134.61 | 542980 NASHUA 7 345 542982 IATAN 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31115 | 134.75 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31116 | 134.67 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31117 | 134.57 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31118 | 134.83 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31119 | 134.58 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31203 | 135.9 | P21:161:OPPD:HUMBOLT-S1398:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31203 | 135.91 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31247 | 135.01 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31247 | 135.12 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31523 | 136.4 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31523 | 136.49 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31597 | 136.54 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31597 | 137.27 | P12:115:WERE:KNOB-MKEC-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31597 | 137.29 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.32881 | 148.17 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34895 | 153.08 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34895 | 153.08 | P13:115-161:NPPD:HUMBOLT5:T2::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34895 | 154.9 | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34895 | 155.51 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34895 | 155.52 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.37252 | 166.49 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.55338 | 242.37 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.38588 | 127.16 | GEN-2023-225_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40152 | 126.11 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40197 | 126.43 | Potential P4 Event - POI 640226_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40208 | 125.8 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4021 | 125.83 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40213 | 125.97 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40213 | 127.04 | Potential P4 Event - POI 640226_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40213 | 127.26 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40214 | 125.86 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40215 | 125.65 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40215 | 126.58 | Potential P4 Event - POI 640226_3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.64 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.65 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.67 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.74 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.76 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.76 | P23:500:EES:PERVIL:R9872 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.76 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.76 | P23:500:EMI:ABF_PRYVL-B | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.77 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.79 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.79 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 126.12 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 126.13 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 126.28 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 126.99 | Potential P4 Event - POI 645740_2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.23 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.36 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.36 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.37 | 509895 T.NO.2-4 138 762636 GEN-2018-028 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.38 | 508286 CAMPCOR4 138 765980 GEN-2021-075 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.38 | 508563 PIRKEY 7 345 769761 GEN-2022-139 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.38 | 514823 ROMNOSE4 138 775201 GEN-2023-161 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.38 | 515150 CANEYCK4 138 769841 GEN-2022-143 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.38 | 525830 TUCO_INT 6 230 525840 ANTELOPE_1 6 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.38 | 526299 LUBBCK_EST 6 230 764875 GEN-2020-060 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.39 | 520893 EL RENO4 138 588720 GEN-2017-117 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.4 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.4 | 514787 DEWEY 4 138 766160 GEN-2021-098 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.4 | 520860 COLBERT4 138 769701 GEN-2022-136 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.4 | 655882 GALAXYTP-MK7 115 659388 KUMMERDG-MK7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.41 | 515055 MAUD 4 138 771742 G22-238XFMR1 34.5 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.41 | 655846 F9______-MK7 115 655872 G9TAP___-MK7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.42 | 523823 CARPENTER 7 345 764980 GEN-2020-008 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.42 | 525481 PLANT_X 6 230 775501 GEN-2023-176 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.42 | 655836 OAKDALE -MK7 115 655853 BEARCREK-MK7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.42 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.42 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.62 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.63 | 511560 GRADY 4 138 511567 CHOCTAW4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.64 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.64 | P12:HV:EES::4SCOTT_1!:4BLOOMFLD%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.65 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.67 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.7 | P12:161:AEPW:EROGERS5:ECNTRTN5::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.7 | P12:161:OKGE:BKRBKR197:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.71 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.74 | P12:161:AEPW-SWPA:BEAVER5:EROGERS5::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.74 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.75 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.75 | P12:HV:EES::6DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.76 | P21:161:ALTW:AUTO-SINGLE:CRYSTLK5:CLKREACT5:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.76 | P21:161:ALTW:AUTO-SINGLE:LIMECKL15:CLKREACT5:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.77 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.78 | P12:161:AEPW:DYESS5:ELMSPRNG:TONTITN5:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.78 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.78 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.81 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.84 | 640119 COL.COG7 115 640028 COLCOG1G 13.8 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.85 | 51993 J2199 SUB 345 3WXFMR J2199 SUB 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.9 | P13:230:UMZW:# 5137 #:: OA IN SD. FAULT ON TRANSFORMER (4).:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.92 | 620322 BSSOUTH4 230 621317 CROWN CAP 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.92 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.93 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.95 | P13:RU901T | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.98 | P13:PR901T GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.98 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.01 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.01 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.02 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.02 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.04 | P21:345:XEL:AUTO-SINGLE:WILMART3:MEC-345:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.06 | P23:345:OTP::TWIN BRKS 3:BRKY_V2021:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.11 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.15 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.15 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.29 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.4 | P23:345:XEL:8P2 KING | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.45 | 645740 S3740 3 345 773564 G23-079GEN1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.45 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.6 | GEN-2021-043_POI_650290_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.61 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.63 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.63 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.63 | P23:345:XEL:8N17 SHC | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.63 | P23:345:XEL:8N22 SHC | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.65 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.67 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.83 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.95 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.04 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.15 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.16 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.17 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.18 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.23 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.27 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.32 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.32 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.32 | Potential P4 Event - POI 640590_11 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.32 | Potential P4 Event - POI 640590_13 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.38 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.39 | Potential P4 Event - POI 659333_5 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.59 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.61 | Potential P4 Event - POI 645740_12 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.97 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 129.14 | GEN-2023-224_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 129.15 | Potential P4 Event - POI 640590_9 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 132.48 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40218 | 125.78 | 542980 NASHUA 7 345 542982 IATAN 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40219 | 125.84 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40219 | 125.92 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4022 | 125.74 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40222 | 125.99 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40223 | 125.75 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40332 | 127.02 | P21:161:OPPD:HUMBOLT-S1398:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40332 | 127.03 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40388 | 126.16 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40388 | 126.27 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40746 | 127.49 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40746 | 127.58 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40841 | 127.63 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40841 | 128.33 | P12:115:WERE:KNOB-MKEC-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40841 | 128.34 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.42501 | 138.75 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45104 | 143.46 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45104 | 145.8 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45104 | 145.81 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4815 | 156.31 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60812 | 189.98 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60812 | 192.94 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60812 | 193.15 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.4 | 771999 G23-222-POI 345 776422 G23-222XFMR1 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.4 | 771999 G23-222-POI 345 776425 G23-222XFMR2 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.4 | 776422 G23-222XFMR1 345 776424 G23-222GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.4 | 776425 G23-222XFMR2 345 776427 G23-222GEN2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.14 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.54 | 772201 GEN-2023-011 115 772202 G23-011XFMR1 34.5 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.54 | GEN-2023-011_POI_640208_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.59 | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.6 | 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.61 | 640208 HARBINE7 115 640426 STEELEC7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.61 | Potential P4 Event - POI 640590_3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.62 | Potential P4 Event - POI 640590_7 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.62 | Potential P4 Event - POI 640590_8 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.63 | P13:115-345:NPPD:MONOLITH 3:T1::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.63 | P13:115-345:NPPD:MONOLITH 3:T2::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.63 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.63 | Potential P4 Event - POI 640525_3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.63 | Potential P4 Event - POI 640525_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.63 | Potential P4 Event - POI 640525_5 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.63 | Potential P4 Event - POI 645740_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.29854 | 133.06 | GEN-2023-225_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31064 | 131.95 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31099 | 132.29 | Potential P4 Event - POI 640226_4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31107 | 131.62 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31109 | 131.65 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31111 | 131.79 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31111 | 132.93 | Potential P4 Event - POI 640226_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31111 | 133.16 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31112 | 131.68 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31113 | 131.44 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31113 | 131.46 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31113 | 131.48 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31113 | 131.96 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31113 | 131.96 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31113 | 132.13 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31113 | 132.45 | Potential P4 Event - POI 640226_3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31113 | 132.89 | Potential P4 Event - POI 645740_2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.01 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.17 | 514823 ROMNOSE4 138 775201 GEN-2023-161 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.17 | 515150 CANEYCK4 138 769841 GEN-2022-143 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.18 | 520893 EL RENO4 138 588720 GEN-2017-117 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.19 | 514787 DEWEY 4 138 766160 GEN-2021-098 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.19 | 520860 COLBERT4 138 769701 GEN-2022-136 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.21 | 301643 FOXTROTGSU 34.5 3WXFMR FOXTROTGSU 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.21 | 523267 PRINGLE 6 230 774441 GEN-2023-123 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.21 | 523309 MOORE_CNTY 6 230 772181 GEN-2023-010 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.21 | 523823 CARPENTER 7 345 764980 GEN-2020-008 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.21 | 526936 YOAKUM 7 345 766120 GEN-2021-090 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.21 | 655840 CHRRYCRK-MK7 115 655876 DPLWCTAP-MK7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.21 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.21 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.22 | 345831 4TAUM S 1 138 345832 1TAUM S G1 13.8 G1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.22 | 345840 4TAUM S 2 138 345841 1TAUM S G2 13.8 G2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.22 | 508359 WELSH 7 345 765660 GEN-2021-038 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.22 | 532772 STRANGR7 345 3WXFMR STRANGR TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.22 | 655876 DPLWCTAP-MK7 115 655877 LITTLMS4-MK7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.22 | 655882 GALAXYTP-MK7 115 655884 DEMCKSLK-MK7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.42 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.42 | 512650 GRDA1 7 345 774740 G23-138-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.43 | 511560 GRADY 4 138 511567 CHOCTAW4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.43 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.44 | P12:HV:EES::4SCOTT_1!:4BLOOMFLD%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.45 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.46 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.46 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.48 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.51 | P12:161:AEPW:EROGERS5:ECNTRTN5::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.52 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.52 | P12:161:OKGE:BKRBKR197:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.56 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.56 | P12:161:AEPW-SWPA:BEAVER5:EROGERS5::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.56 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.56 | P12:HV:EES::6DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.56 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.58 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.58 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.58 | P21:161:ALTW:AUTO-SINGLE:CRYSTLK5:CLKREACT5:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.58 | P21:161:ALTW:AUTO-SINGLE:LIMECKL15:CLKREACT5:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.58 | P23:500:EES:PERVIL:R9872 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.58 | P23:500:EMI:ABF_PRYVL-A | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.59 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.59 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.6 | P12:161:AEPW:DYESS5:ELMSPRNG:TONTITN5:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.6 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.6 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.6 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.6 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.62 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.65 | 640119 COL.COG7 115 640028 COLCOG1G 13.8 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.67 | 51993 J2199 SUB 345 3WXFMR J2199 SUB 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.73 | P13:230:UMZW:# 5137 #:: OA IN SD. FAULT ON TRANSFORMER (4).:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.74 | 620322 BSSOUTH4 230 621317 CROWN CAP 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.74 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.76 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.78 | P13:RU901T | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.81 | P13:PR901T GSU | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.81 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.83 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.84 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.84 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.85 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.85 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.87 | P21:345:XEL:AUTO-SINGLE:WILMART3:MEC-345:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.89 | P23:345:OTP::TWIN BRKS 3:BRKY_V2021:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.9 | P11:18:SPC:PR#1:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.95 | P11:024:DPC:ALMA2:6 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.98 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.99 | P12:138:OKGE:BKRBKR130:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.14 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.25 | P23:345:XEL:8P2 KING | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.27 | P11:18:SPC: BD #6+SSL:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.31 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.35 | P11:18:SPC: BD #6:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.43 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.47 | GEN-2021-043_POI_650290_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.48 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.5 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.5 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.5 | P23:345:XEL:8N17 SHC | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.5 | P23:345:XEL:8N22 SHC | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.52 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.54 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.55 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.58 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.58 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.71 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.84 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.94 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.05 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.07 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.07 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.08 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.14 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.18 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.24 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.24 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.24 | Potential P4 Event - POI 640590_10 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.24 | Potential P4 Event - POI 640590_12 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.3 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.31 | Potential P4 Event - POI 659333_5 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.52 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.54 | Potential P4 Event - POI 645740_12 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.93 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 134.78 | 640112 CLATONA9 34.5 3WXFMR CLATONIA T1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 135.18 | GEN-2023-224_POI_640590_Generator_outage | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 135.18 | Potential P4 Event - POI 640590_9 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 138.74 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31115 | 131.6 | 542980 NASHUA 7 345 542982 IATAN 7 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31115 | 131.74 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31116 | 131.66 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31117 | 131.55 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31118 | 131.82 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31119 | 131.57 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31203 | 132.92 | P21:161:OPPD:HUMBOLT-S1398:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31203 | 132.93 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31247 | 132 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31247 | 132.12 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31523 | 133.41 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31523 | 133.51 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31597 | 133.56 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31597 | 134.31 | P12:115:WERE:KNOB-MKEC-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31597 | 134.32 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.32881 | 145.41 | P12:115:WERE:KNOB-NPPD-115:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34895 | 150.44 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34895 | 150.44 | P13:115-161:NPPD:HUMBOLT5:T2::: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34895 | 152.31 | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34895 | 152.93 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34895 | 152.94 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.37252 | 164.13 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.55338 | 241.55 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.04 | 771999 G23-222-POI 345 776422 G23-222XFMR1 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.04 | 771999 G23-222-POI 345 776425 G23-222XFMR2 345 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.04 | 776422 G23-222XFMR1 345 776424 G23-222GEN1 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.04 | 776425 G23-222XFMR2 345 776427 G23-222GEN2 18.0 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 171.1 | Potential P4 Event - POI 640590_0 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 171.12 | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 171.12 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 171.13 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 171.41 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 171.44 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 171.44 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 171.47 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | TDF Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.54961 | 105.32 | P42:345:OPPD-LES:S3454-S3455&WAG:::EHV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.57209 | 113.2 | P42:345:MEC-OPPD:S3456-S3458&CBL:::EHV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.57209 | 113.2 | P45:345:OPPD:S3456-S3458&CBL:::EHV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.59009 | 111.84 | P12:345:OPPD:LX007::S3458.S3456.CKT1:: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.59407 | 106.09 | 635200 RAUN 3 345 762779 G18-043 TAP 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.59407 | 107.18 | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.59407 | 107.18 | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.59571 | 104.59 | P21:345:MEC-OPPD:AUTO-SINGLE:CBLUFFS3:S34563:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.6032 | 109.01 | P23:345:MEC:CBEC 905 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 106.69 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 106.69 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 106.83 | P23:345:MEC:ATCHISON CO 903 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 107.07 | 635017 ATCHISON 3 345 635018 WESTBORO 3 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 107.34 | Potential P4 Event - POI 635018_0 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 107.34 | Potential P4 Event - POI 635018_1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 107.34 | Potential P4 Event - POI 635018_2 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 107.74 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60424 | 105.07 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60432 | 104.34 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60432 | 104.68 | P23:345:AMMO:::24SPENCERCREEK:EHV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60446 | 104.24 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60475 | 104.37 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60488 | 104.34 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.6049 | 108.85 | P23:345:MEC:CBEC 908 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60492 | 104.23 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60492 | 104.38 | P12:345:WERE:N345-AECI-345:::EHV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60493 | 104.25 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60495 | 104.29 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60495 | 104.29 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60495 | 104.3 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60496 | 104.39 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60496 | 104.39 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60496 | 104.39 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60497 | 104.14 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60497 | 104.19 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60497 | 104.26 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.15 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.17 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.18 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.19 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.42 | P12:500:EES-EAI:DRIVER:SHELBY | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.42 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.49 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.49 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.03 | 515853 DGRASSE4 138 763769 GEN-2019-045 138 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.11 | 520826 BENNGTN4 138 521115 BENNSUB4 138 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.11 | P12:HV:EES::3VIENNA_LA!:3RUSTON:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.11 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.12 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.12 | 514722 CLEVETP2 69.0 514723 CLEVLND2 69.0 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.14 | 515149 MADINDT4 138 515158 MADLIND4 138 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 346093 2LATHROP 69.0 344923 5LATHROP 161 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 523143 NP-PERDUR_G3 115 523186 SPEARMAN 3 115 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 523186 SPEARMAN 3 115 3WXFMR VON 13770/1 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 525731 SP-ABNTYPOI2 69.0 525816 TUCO_INT2 2 69.0 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.16 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.17 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.19 | 509829 FULTONW4 138 509830 KENSH-E-TP4 138 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.22 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.23 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.25 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.26 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.26 | P12:161:OKGE:BKRBKR197:::: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.3 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.33 | 635580 ARBOR HILL 3 345 635582 ARBR HL B2 9 34.5 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.33 | P12:HV:EES::6DRIVER%:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.37 | 646211 S1211 5 161 645023 N OMA 3G 13.8 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.39 | P12:115:WERE:EMAN-KSU-115:::HV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.39 | P13:138-115:MP:TCH:TR4(1) | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.42 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.42 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.44 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.48 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.5 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.56 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.57 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.57 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.59 | P13:NBEC#1 GSU | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.63 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.68 | P13:SH902T GSU | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.69 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.7 | P12:138:OKGE:BKRBKR130:::: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.72 | 762712 G18-037-TAP 161 762713 GEN-2018-037 161 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.72 | P11:18:SPC: BD #6+SSL:::HV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.77 | P11:18:SPC: BD #6:::HV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.79 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.8 | P11:024:DPC:ALMA2:6 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.91 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.99 | 764601 G20-025-GEN1 20.0 764600 GEN-2020-025 161 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.99 | 775961 GEN-2023-199 230 775962 G23-199XFMR1 34.5 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.99 | GEN-2020-028_POI_646363_Generator_outage | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.99 | GEN-2023-199_POI_640386_Generator_outage | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.04 | 762779 G18-043 TAP 345 762780 GEN-2018-043 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.08 | 764661 G20-031-GEN1 20.0 764660 GEN-2020-031 161 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.08 | GEN-2020-031_POI_646363_Generator_outage | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.24 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.25 | P11:20:XEL:AUTO-SINGLE:KING31G:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.28 | P23:345:XEL:8H14 PRI | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.3 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.3 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.35 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.48 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.49 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.5 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.54 | P23:345:XEL:8N8 MNN | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.58 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.58 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.9 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 106.01 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 106.23 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 106.83 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 106.98 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 108.9 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 109.21 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 109.42 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 110.09 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.605 | 104.19 | 344536 7ENON_TP 345 345217 7ROOTBEER 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.605 | 104.2 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60504 | 104.34 | P12:345:OKGE:BKRBKR357_1:::: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60506 | 104.17 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60509 | 104.21 | 532791 BENTON 7 345 766141 G21-096-TAP 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60511 | 104.13 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60511 | 104.28 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60555 | 104.6 | 767240 G22-013-TAP 345 776600 G23-231-TAP 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60555 | 104.95 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60566 | 104.26 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.6057 | 105.04 | 300076 5FAIRPTB2 161 301559 5FAIRPTXF3 161 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.6057 | 105.04 | 301559 5FAIRPTXF3 161 300039 7FAIRPT 345 3 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60601 | 104.24 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60648 | 104.75 | 300039 7FAIRPT 345 640139 COOPER 3 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.6074 | 108.19 | P42:345:NPPD:BKR-CPR-3304:::: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.57 | Potential P4 Event - POI 541510_3 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.78 | Potential P4 Event - POI 541510_1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.8 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.82 | 541197 MULLNCR7 345 541510 HOLT 7 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.82 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.82 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.87 | 541197 MULLNCR7 345 771140 G22-208-TAP 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61786 | 106.38 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61786 | 106.39 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61786 | 106.45 | Potential P4 Event - POI 541510_0 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 119.18 | Potential P4 Event - POI 645740_10 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 134.5 | Potential P4 Event - POI 645740_11 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.54 | P12:345:OPPD:LX008::S3458.S3740.CKT1:: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.54 | P22:345:OPPD:S3458-S3740:::EHV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.54 | P22:345:OPPD:S3740-S3458:::EHV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.54 | P23:345:OPPD:S3740-S3458:::EHV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.54 | Potential P4 Event - POI 645740_1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 132.46 | Potential P4 Event - POI 645740_7 | Cumulative Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 149.89 | Potential P4 Event - POI 645740_8 | Cumulative Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 156.81 | P12:345:OPPD:S3455-S3740:::EHV: | Cumulative Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 156.81 | P22:345:OPPD:S3455-S3740:::EHV: | Cumulative Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 156.81 | P23:345:OPPD:S3455-S3740:::EHV: | Cumulative Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 156.81 | Potential P4 Event - POI 645740_0 | Cumulative Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99998 | 147.02 | P41:345:OPPD:S3740-55&CC2:::EHV: | Cumulative Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99998 | 147.02 | P43:015-345:OPPD:S3740-S3455&CC2:::HV: | Cumulative Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-077 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99998 | 147.02 | P45:345:OPPD:S3740-S3455&CC2:::EHV: | Cumulative Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.54961 | 105.32 | P42:345:OPPD-LES:S3454-S3455&WAG:::EHV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.57209 | 113.2 | P42:345:MEC-OPPD:S3456-S3458&CBL:::EHV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.57209 | 113.2 | P45:345:OPPD:S3456-S3458&CBL:::EHV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.59009 | 111.84 | P12:345:OPPD:LX007::S3458.S3456.CKT1:: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.59407 | 106.09 | 635200 RAUN 3 345 762779 G18-043 TAP 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.59407 | 107.18 | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.59407 | 107.18 | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.59571 | 104.59 | P21:345:MEC-OPPD:AUTO-SINGLE:CBLUFFS3:S34563:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.6032 | 109.01 | P23:345:MEC:CBEC 905 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 106.69 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 106.69 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 106.83 | P23:345:MEC:ATCHISON CO 903 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 107.07 | 635017 ATCHISON 3 345 635018 WESTBORO 3 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 107.34 | Potential P4 Event - POI 635018_0 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 107.34 | Potential P4 Event - POI 635018_1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 107.34 | Potential P4 Event - POI 635018_2 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 107.74 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60424 | 105.07 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60432 | 104.34 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60432 | 104.68 | P23:345:AMMO:::24SPENCERCREEK:EHV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60446 | 104.24 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60475 | 104.37 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60488 | 104.34 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.6049 | 108.85 | P23:345:MEC:CBEC 908 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60492 | 104.23 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60492 | 104.38 | P12:345:WERE:N345-AECI-345:::EHV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60493 | 104.25 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60495 | 104.29 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60495 | 104.29 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60495 | 104.3 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60496 | 104.39 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60496 | 104.39 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60496 | 104.39 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60497 | 104.14 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60497 | 104.19 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60497 | 104.26 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.15 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.17 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.18 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.19 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.42 | P12:500:EES-EAI:DRIVER:SHELBY | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.42 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.49 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.49 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.03 | 515853 DGRASSE4 138 763769 GEN-2019-045 138 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.11 | 520826 BENNGTN4 138 521115 BENNSUB4 138 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.11 | P12:HV:EES::3VIENNA_LA!:3RUSTON:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.11 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.12 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.12 | 514722 CLEVETP2 69.0 514723 CLEVLND2 69.0 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.14 | 515149 MADINDT4 138 515158 MADLIND4 138 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 346093 2LATHROP 69.0 344923 5LATHROP 161 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 523143 NP-PERDUR_G3 115 523186 SPEARMAN 3 115 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 523186 SPEARMAN 3 115 3WXFMR VON 13770/1 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 525731 SP-ABNTYPOI2 69.0 525816 TUCO_INT2 2 69.0 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.16 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.17 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.19 | 509829 FULTONW4 138 509830 KENSH-E-TP4 138 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.22 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.23 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.25 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.26 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.26 | P12:161:OKGE:BKRBKR197:::: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.3 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.33 | 635580 ARBOR HILL 3 345 635582 ARBR HL B2 9 34.5 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.33 | P12:HV:EES::6DRIVER%:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.37 | 646211 S1211 5 161 645023 N OMA 3G 13.8 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.39 | P12:115:WERE:EMAN-KSU-115:::HV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.39 | P13:138-115:MP:TCH:TR4(1) | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.42 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.42 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.44 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.48 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.5 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.56 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.57 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.57 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.59 | P13:NBEC#1 GSU | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.63 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.68 | P13:SH902T GSU | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.69 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.7 | P12:138:OKGE:BKRBKR130:::: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.72 | 762712 G18-037-TAP 161 762713 GEN-2018-037 161 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.72 | P11:18:SPC: BD #6+SSL:::HV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.77 | P11:18:SPC: BD #6:::HV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.79 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.8 | P11:024:DPC:ALMA2:6 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.91 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.99 | 764601 G20-025-GEN1 20.0 764600 GEN-2020-025 161 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.99 | 775961 GEN-2023-199 230 775962 G23-199XFMR1 34.5 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.99 | GEN-2020-028_POI_646363_Generator_outage | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.99 | GEN-2023-199_POI_640386_Generator_outage | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.04 | 762779 G18-043 TAP 345 762780 GEN-2018-043 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.08 | 764661 G20-031-GEN1 20.0 764660 GEN-2020-031 161 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.08 | GEN-2020-031_POI_646363_Generator_outage | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.24 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.25 | P11:20:XEL:AUTO-SINGLE:KING31G:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.28 | P23:345:XEL:8H14 PRI | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.3 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.3 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.35 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.48 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.49 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.5 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.54 | P23:345:XEL:8N8 MNN | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.58 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.58 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.9 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 106.01 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 106.23 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 106.83 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 106.98 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 108.9 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 109.21 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 109.42 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 110.09 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.605 | 104.19 | 344536 7ENON_TP 345 345217 7ROOTBEER 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.605 | 104.2 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60504 | 104.34 | P12:345:OKGE:BKRBKR357_1:::: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60506 | 104.17 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60509 | 104.21 | 532791 BENTON 7 345 766141 G21-096-TAP 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60511 | 104.13 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60511 | 104.28 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60555 | 104.6 | 767240 G22-013-TAP 345 776600 G23-231-TAP 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60555 | 104.95 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60566 | 104.26 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.6057 | 105.04 | 300076 5FAIRPTB2 161 301559 5FAIRPTXF3 161 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.6057 | 105.04 | 301559 5FAIRPTXF3 161 300039 7FAIRPT 345 3 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60601 | 104.24 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60648 | 104.75 | 300039 7FAIRPT 345 640139 COOPER 3 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.6074 | 108.19 | P42:345:NPPD:BKR-CPR-3304:::: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.57 | Potential P4 Event - POI 541510_3 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.78 | Potential P4 Event - POI 541510_1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.8 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.82 | 541197 MULLNCR7 345 541510 HOLT 7 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.82 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.82 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.87 | 541197 MULLNCR7 345 771140 G22-208-TAP 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61786 | 106.38 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61786 | 106.39 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61786 | 106.45 | Potential P4 Event - POI 541510_0 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 119.18 | Potential P4 Event - POI 645740_10 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 134.5 | Potential P4 Event - POI 645740_11 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.54 | P12:345:OPPD:LX008::S3458.S3740.CKT1:: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.54 | P22:345:OPPD:S3458-S3740:::EHV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.54 | P22:345:OPPD:S3740-S3458:::EHV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.54 | P23:345:OPPD:S3740-S3458:::EHV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.54 | Potential P4 Event - POI 645740_1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 132.46 | Potential P4 Event - POI 645740_7 | Cumulative Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 149.89 | Potential P4 Event - POI 645740_8 | Cumulative Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 156.81 | P12:345:OPPD:S3455-S3740:::EHV: | Cumulative Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 156.81 | P22:345:OPPD:S3455-S3740:::EHV: | Cumulative Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 156.81 | P23:345:OPPD:S3455-S3740:::EHV: | Cumulative Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 156.81 | Potential P4 Event - POI 645740_0 | Cumulative Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99998 | 147.02 | P41:345:OPPD:S3740-55&CC2:::EHV: | Cumulative Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99998 | 147.02 | P43:015-345:OPPD:S3740-S3455&CC2:::HV: | Cumulative Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-078 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99998 | 147.02 | P45:345:OPPD:S3740-S3455&CC2:::EHV: | Cumulative Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.54961 | 105.32 | P42:345:OPPD-LES:S3454-S3455&WAG:::EHV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.57209 | 113.2 | P42:345:MEC-OPPD:S3456-S3458&CBL:::EHV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.57209 | 113.2 | P45:345:OPPD:S3456-S3458&CBL:::EHV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.59009 | 111.84 | P12:345:OPPD:LX007::S3458.S3456.CKT1:: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.59407 | 106.09 | 635200 RAUN 3 345 762779 G18-043 TAP 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.59407 | 107.18 | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.59407 | 107.18 | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.59571 | 104.59 | P21:345:MEC-OPPD:AUTO-SINGLE:CBLUFFS3:S34563:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.6032 | 109.01 | P23:345:MEC:CBEC 905 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 106.69 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 106.69 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 106.83 | P23:345:MEC:ATCHISON CO 903 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 107.07 | 635017 ATCHISON 3 345 635018 WESTBORO 3 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 107.34 | Potential P4 Event - POI 635018_0 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 107.34 | Potential P4 Event - POI 635018_1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 107.34 | Potential P4 Event - POI 635018_2 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60374 | 107.74 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60424 | 105.07 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60432 | 104.34 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60432 | 104.68 | P23:345:AMMO:::24SPENCERCREEK:EHV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60446 | 104.24 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60475 | 104.37 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60488 | 104.34 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.6049 | 108.85 | P23:345:MEC:CBEC 908 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60492 | 104.23 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60492 | 104.38 | P12:345:WERE:N345-AECI-345:::EHV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60493 | 104.25 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60495 | 104.29 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60495 | 104.29 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60495 | 104.3 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60496 | 104.39 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60496 | 104.39 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60496 | 104.39 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60497 | 104.14 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60497 | 104.19 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60497 | 104.26 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.15 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.17 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.18 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.19 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.42 | P12:500:EES-EAI:DRIVER:SHELBY | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.42 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.49 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60498 | 104.49 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.03 | 515853 DGRASSE4 138 763769 GEN-2019-045 138 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.11 | 520826 BENNGTN4 138 521115 BENNSUB4 138 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.11 | P12:HV:EES::3VIENNA_LA!:3RUSTON:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.11 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.12 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.12 | 514722 CLEVETP2 69.0 514723 CLEVLND2 69.0 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.14 | 515149 MADINDT4 138 515158 MADLIND4 138 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 346093 2LATHROP 69.0 344923 5LATHROP 161 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 523143 NP-PERDUR_G3 115 523186 SPEARMAN 3 115 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 523186 SPEARMAN 3 115 3WXFMR VON 13770/1 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 525731 SP-ABNTYPOI2 69.0 525816 TUCO_INT2 2 69.0 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.15 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.16 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.17 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.19 | 509829 FULTONW4 138 509830 KENSH-E-TP4 138 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.22 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.23 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.25 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.26 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.26 | P12:161:OKGE:BKRBKR197:::: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.3 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.33 | 635580 ARBOR HILL 3 345 635582 ARBR HL B2 9 34.5 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.33 | P12:HV:EES::6DRIVER%:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.37 | 646211 S1211 5 161 645023 N OMA 3G 13.8 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.39 | P12:115:WERE:EMAN-KSU-115:::HV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.39 | P13:138-115:MP:TCH:TR4(1) | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.42 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.42 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.44 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.48 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.5 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.56 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.57 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.57 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.59 | P13:NBEC#1 GSU | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.63 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.68 | P13:SH902T GSU | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.69 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.7 | P12:138:OKGE:BKRBKR130:::: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.72 | 762712 G18-037-TAP 161 762713 GEN-2018-037 161 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.72 | P11:18:SPC: BD #6+SSL:::HV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.77 | P11:18:SPC: BD #6:::HV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.79 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.8 | P11:024:DPC:ALMA2:6 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.91 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.99 | 764601 G20-025-GEN1 20.0 764600 GEN-2020-025 161 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.99 | 775961 GEN-2023-199 230 775962 G23-199XFMR1 34.5 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.99 | GEN-2020-028_POI_646363_Generator_outage | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 104.99 | GEN-2023-199_POI_640386_Generator_outage | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.04 | 762779 G18-043 TAP 345 762780 GEN-2018-043 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.08 | 764661 G20-031-GEN1 20.0 764660 GEN-2020-031 161 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.08 | GEN-2020-031_POI_646363_Generator_outage | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.24 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.25 | P11:20:XEL:AUTO-SINGLE:KING31G:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.28 | P23:345:XEL:8H14 PRI | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.3 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.3 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.35 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.48 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.49 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.5 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.54 | P23:345:XEL:8N8 MNN | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.58 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.58 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 105.9 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 106.01 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 106.23 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 106.83 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 106.98 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 108.9 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 109.21 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 109.42 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60499 | 110.09 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.605 | 104.19 | 344536 7ENON_TP 345 345217 7ROOTBEER 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.605 | 104.2 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60504 | 104.34 | P12:345:OKGE:BKRBKR357_1:::: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60506 | 104.17 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60509 | 104.21 | 532791 BENTON 7 345 766141 G21-096-TAP 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60511 | 104.13 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60511 | 104.28 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60555 | 104.6 | 767240 G22-013-TAP 345 776600 G23-231-TAP 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60555 | 104.95 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60566 | 104.26 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.6057 | 105.04 | 300076 5FAIRPTB2 161 301559 5FAIRPTXF3 161 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.6057 | 105.04 | 301559 5FAIRPTXF3 161 300039 7FAIRPT 345 3 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60601 | 104.24 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60648 | 104.75 | 300039 7FAIRPT 345 640139 COOPER 3 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.6074 | 108.19 | P42:345:NPPD:BKR-CPR-3304:::: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.57 | Potential P4 Event - POI 541510_3 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.78 | Potential P4 Event - POI 541510_1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.8 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.82 | 541197 MULLNCR7 345 541510 HOLT 7 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.82 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREA:::EHV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.82 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT_1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61785 | 106.87 | 541197 MULLNCR7 345 771140 G22-208-TAP 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61786 | 106.38 | 645458 S3458 3 345 645558 S3458-HOLT 3 345 Z1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61786 | 106.39 | 541510 HOLT 7 345 645558 S3458-HOLT 3 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.61786 | 106.45 | Potential P4 Event - POI 541510_0 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 119.18 | Potential P4 Event - POI 645740_10 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 134.5 | Potential P4 Event - POI 645740_11 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.54 | P12:345:OPPD:LX008::S3458.S3740.CKT1:: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.54 | P22:345:OPPD:S3458-S3740:::EHV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.54 | P22:345:OPPD:S3740-S3458:::EHV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.54 | P23:345:OPPD:S3740-S3458:::EHV: | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.54 | Potential P4 Event - POI 645740_1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 132.46 | Potential P4 Event - POI 645740_7 | Cumulative Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 149.89 | Potential P4 Event - POI 645740_8 | Cumulative Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 156.81 | P12:345:OPPD:S3455-S3740:::EHV: | Cumulative Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 156.81 | P22:345:OPPD:S3455-S3740:::EHV: | Cumulative Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 156.81 | P23:345:OPPD:S3455-S3740:::EHV: | Cumulative Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 156.81 | Potential P4 Event - POI 645740_0 | Cumulative Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99998 | 147.02 | P41:345:OPPD:S3740-55&CC2:::EHV: | Cumulative Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99998 | 147.02 | P43:015-345:OPPD:S3740-S3455&CC2:::HV: | Cumulative Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-079 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99998 | 147.02 | P45:345:OPPD:S3740-S3455&CC2:::EHV: | Cumulative Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | 193 | 193 | 0.27216 | 140.8 | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 193 | 193 | 0.22811 | 101.78 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 193 | 193 | 0.27331 | 141.4 | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.16843 | 149.47 | P13:115-230:SUNC:CONCORDIA_XFR:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17125 | 144.07 | 539805 ELMCREEK7 345 3WXFMR ELMCREEK T1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17194 | 143.74 | 532765 HOYT 7 345 3WXFMR HOYT1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1721 | 143.82 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17212 | 143.37 | P42:345:OKGE:SB_RARD7381:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17212 | 145.56 | Potential P4 Event - POI 515576_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 141.87 | P13:69-161:XEL:AUTO-SINGLE:WBYRON8:BYRON5:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 141.95 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 141.95 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.03 | P12:115:XEL:AUTO-SINGLE:NSSTAP7:NSSTL7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.03 | P21:115:XEL:AUTO-SINGLE:NSSTAP7:NSSTL7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.08 | P12:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.08 | P21:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.12 | P21:115:XEL:AUTO-SINGLE:REDROCK7:NSSJCT7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.14 | 506944 CHAMSPR5 161 776241 GEN-2023-213 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.15 | 512635 KERR GR5 161 773081 GEN-2023-055 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.15 | 528013 PHANTOM 3 115 775661 GEN-2023-184 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.15 | P12:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.16 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.19 | 508298 LYDIA 7 345 764075 GEN-2020-054 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.21 | P12:345:XEL:ASK-ECL SPS | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.22 | 505522 VAN BUR5 161 773101 GEN-2023-056 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.23 | 526936 YOAKUM 7 345 766120 GEN-2021-090 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.24 | 515235 PECANCK7 345 762823 GEN-2018-048 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.24 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.25 | 659387 KUMMERDG-BE3 345 659390 PATENTGT-BE3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.28 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.31 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.36 | 509782 R.S.S.-7 345 588040 G16133G16146 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.38 | 300024 1CHOTST6 16.0 301348 5CHOTEAU2 161 20 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.38 | 300031 1CHOTST3 16.0 300069 5CHOTEAU1 161 10 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.4 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.5 | 512749 PAWNSW4 138 773121 GEN-2023-057 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.6 | P13:161-22:AEPW:FLINTCR5:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.68 | 514922 CLASSEN4 138 775341 GEN-2023-168 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.73 | 640112 CLATONA9 34.5 3WXFMR CLATONIA T1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.75 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.77 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.77 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.77 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.81 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.81 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.83 | P13:345:GRDA:GRDA2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.85 | P12:161:GRDA:SALINA 5-SALNCRK5:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.86 | 560053 G15052_T 345 562900 G15052_1 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.88 | P13:138-24:AEPW:TURK 4:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.9 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.91 | P13:345-22:AEPW:N.E.S.-7_#1:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.98 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.99 | P23:500:EES-EAI:WH_BLF:B7942 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.02 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.03 | P23:345:AEPW:NES CB 3417B NBTB:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.06 | P23:345:AEPW:NES CB 3413B NBTB:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.06 | P41:345:AEPW:NES CB 3413B NBTB+FAULT:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.08 | 515156 WASHPRK4 138 775321 GEN-2023-167 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.13 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.28 | 776061 GEN-2023-204 345 776064 G23-204GEN1 23.5 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.38 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.39 | 525481 PLANT_X 6 230 774821 GEN-2023-142 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.4 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.41 | 532793 NEOSHO 7 345 772981 GEN-2023-050 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.5 | 532766 JEC N 7 345 766240 GEN-2021-107 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.52 | 515852 DGRASSE7 345 773981 GEN-2023-100 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.55 | 527000 GAINES_PLNT7 345 527020 SIDEWINDER 7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.59 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.63 | P13:115:WERE:EMAN-TX-3-230-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.64 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.87 | P11:HV:EES::1RVR_BND_G1!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.87 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.87 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.87 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.91 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.96 | 525832 TUCO_INT 7 345 525850 ELK_CT1 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.96 | 525832 TUCO_INT 7 345 769921 GEN-2022-147 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.97 | 515800 GRACMNT7 345 775261 GEN-2023-164 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 144 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 144.11 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 144.11 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 144.12 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 144.15 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 144.21 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 144.24 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 144.24 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 144.31 | 515852 DGRASSE7 345 776821 GEN-2023-102 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 144.31 | GEN-2023-102_POI_515852_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 144.34 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 144.34 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 144.88 | 776060 G23-204-TAP 345 776061 GEN-2023-204 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 144.89 | GEN-2023-204_POI_776060_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 144.97 | Potential P4 Event - POI 515576_20 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 145.13 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 146.22 | 640218 HEBRN N7 115 640012 HEBRON G 13.8 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 146.26 | Potential P4 Event - POI 525832_3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 147.62 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 149.29 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 161.56 | 640208 HARBINE7 115 772201 GEN-2023-011 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 161.56 | 772201 GEN-2023-011 115 772202 G23-011XFMR1 34.5 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 161.56 | GEN-2023-011_POI_640208_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 141.89 | 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 141.91 | 338120 5S.LEAD HILL 161 505461 BULL SH W5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 142.23 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:HCKRYCK3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 142.29 | P23:345:ITCM:HAZLTON3 9985:IA-NE | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 142.32 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 142.36 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 149.33 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17216 | 142.13 | P12:345:XEL:AUTO-SINGLE:WILMART3:SHEASLK3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17216 | 142.61 | P23:345:AEPW:VALLIANT CB 3421A NBTB:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17216 | 142.98 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 143.69 | P42:500:OKGE:SB_FTTH8581:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 143.69 | P42:500:OKGE:SB_FTTH8585:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 143.71 | P12:500:OKGE-EESAR:OKGE-EESEAI:BKRBKR317::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 143.71 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17221 | 142.62 | 300041 7FRANKS 345 300051 7FRANKSRCTP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17221 | 142.63 | 300042 7HUBEN 345 300051 7FRANKSRCTP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17223 | 142.55 | 635580 ARBOR HILL 3 345 635590 FALLOW AVE 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17223 | 142.93 | 635580 ARBOR HILL 3 345 635622 RCCN TRL 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1723 | 143.89 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1723 | 143.89 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1723 | 143.92 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17235 | 142.43 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17235 | 142.64 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17235 | 142.64 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17235 | 142.64 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17235 | 142.64 | P23:345:MEC:BONDURANT 906 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17235 | 142.64 | P23:345:MEC:BONDURANT:903::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17235 | 142.64 | P23:345:MEC:BONDURANT:906::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17235 | 143.04 | P23:345:MEC:MONTEZUMA:902::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17259 | 143.99 | 300039 7FAIRPT 345 640139 COOPER 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17273 | 144.44 | 541197 MULLNCR7 345 771140 G22-208-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17273 | 144.44 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17273 | 144.48 | 541197 MULLNCR7 345 541510 HOLT 7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17277 | 146.26 | Potential P4 Event - POI 532772_9 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17298 | 149.99 | 532913 KELLY 5 161 3WXFMR KELL TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.173 | 145.52 | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1732 | 146.09 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1732 | 146.09 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17497 | 152.69 | P12:161:WERE:TECH-KELL-OPPD-161:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17497 | 152.69 | P12:161:WERE-OPPD:S1399-KELLY:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17513 | 146.93 | Potential P4 Event - POI 640271_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17672 | 152.06 | P21:161:OPPD:S1399-KELLY:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17766 | 152.52 | Potential P4 Event - POI 640590_7 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17766 | 152.52 | Potential P4 Event - POI 640590_8 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17929 | 147.26 | Potential P4 Event - POI 640271_1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.18703 | 166.39 | Potential P4 Event - POI 640590_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.19983 | 159.5 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.19983 | 161.27 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.23425 | 177.76 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.23425 | 179.69 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.23425 | 179.94 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.26657 | 200.2 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640361 STEINER7 115 1 | 121 | 121 | 0.17938 | 104.23 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.29875 | 141.91 | GEN-2023-225_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31104 | 141 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31135 | 141.21 | Potential P4 Event - POI 640226_4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31142 | 140.27 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.75 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31146 | 140.26 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31147 | 142.07 | P23:345:MEC:CBEC 905 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 140.24 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 140.38 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 140.44 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 140.45 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 140.46 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 140.54 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 140.8 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 141.25 | Potential P4 Event - POI 640226_3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 141.96 | Potential P4 Event - POI 640226_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.81 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.92 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.92 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.95 | 515802 GRACMNT4 138 774981 GEN-2023-150 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.96 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.96 | 515543 RENFROW7 345 760809 GEN-2017-203 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.96 | 655845 GRDNCRK2-MK7 115 655879 OASIS___-MK7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.97 | 514801 MINCO 7 345 761250 GEN-2017-233 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.97 | 523267 PRINGLE 6 230 774441 GEN-2023-123 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.97 | 523309 MOORE_CNTY 6 230 772181 GEN-2023-010 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.97 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.97 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.18 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.18 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.18 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.18 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.19 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.19 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.2 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.2 | 509829 FULTONW4 138 509830 KENSH-E-TP4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.21 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.21 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.21 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.22 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.24 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.25 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.26 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.27 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.27 | P12:138:OKGE:BKRBKR176:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.27 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.28 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.28 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.33 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.34 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.34 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.34 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.35 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.35 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.39 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.39 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.4 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.41 | 48983 J1898 SUB 161 3WXFMR J1898 SUB 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.41 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.41 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.41 | P23:500:EES:PERVIL:R9872 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.41 | P23:500:EMI:ABF_PRYVL-A | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.42 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.44 | 51993 J2199 SUB 345 3WXFMR J2199 SUB 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.45 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.45 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.5 | 762779 G18-043 TAP 345 762780 GEN-2018-043 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.53 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.56 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.56 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.56 | P13:NBEC#1 GSU | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.57 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.58 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.64 | P13:SH902T GSU | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.67 | P11:024:DPC:ALMA2:6 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.67 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.67 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.67 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.68 | P11:18:SPC: BD #6+SSL:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.72 | P11:18:SPC: BD #6:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.79 | P12:138:OKGE:BKRBKR130:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.88 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.05 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.07 | P23:345:XEL:8H14 PRI | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.08 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.09 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.13 | GEN-2021-043_POI_650290_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.26 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.27 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.27 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.27 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.27 | P23:345:XEL:8N22 SHC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.3 | 640427 STEELEC9 4.16 640426 STEELEC7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.31 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.35 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.35 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.37 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.45 | P23:345:OPPD:S3740-S3455&CC2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.45 | P41:345:OPPD:S3740-55&CC2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.45 | P42:345:OPPD:S3740-S3455&CC2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.45 | P43:015-345:OPPD:S3740-S3455&CC2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.59 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.61 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.71 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.91 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.94 | P23:345:MEC:CBEC 908 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.95 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.01 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.05 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.11 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.11 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.11 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.11 | Potential P4 Event - POI 640590_12 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.11 | Potential P4 Event - POI 640590_13 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.18 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.26 | Potential P4 Event - POI 645740_6 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.3 | Potential P4 Event - POI 645740_12 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.41 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 143.96 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 144.16 | GEN-2023-224_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 144.16 | Potential P4 Event - POI 640590_9 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 146.12 | Potential P4 Event - POI 645740_5 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 146.58 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3115 | 140.24 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3115 | 140.25 | 512694 CLEVLND7 345 560056 G15066_T 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3115 | 140.44 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3115 | 140.48 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31151 | 140.18 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31151 | 140.53 | P12:345:OKGE:BKRBKR357_1:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31151 | 140.57 | P42:345:OKGE:SB_SOER7383:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31153 | 140.34 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31154 | 140.35 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31154 | 140.43 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31167 | 140.3 | P12:115:HAST:::LINE | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31233 | 141.42 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31276 | 140.7 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31276 | 140.72 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31552 | 141.97 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31552 | 142.1 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31621 | 141.76 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31621 | 142.62 | P12:115:WERE:KNOB-MKEC-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31621 | 142.64 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.32883 | 154.35 | P12:115:WERE:KNOB-NPPD-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34903 | 157.75 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34903 | 157.75 | P13:115-161:NPPD:HUMBOLT5:T2::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34903 | 159.08 | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34903 | 159.51 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34903 | 159.53 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.37286 | 175.27 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.55406 | 247.71 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.38615 | 132.39 | GEN-2023-225_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40204 | 131.52 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40244 | 131.71 | Potential P4 Event - POI 640226_4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40253 | 130.82 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40257 | 130.81 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40257 | 131.28 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40259 | 132.54 | P23:345:MEC:CBEC 905 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4026 | 131.01 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4026 | 131.33 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4026 | 132.43 | Potential P4 Event - POI 640226_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40261 | 130.79 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40261 | 130.81 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40261 | 130.93 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40261 | 130.99 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40261 | 130.99 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40261 | 131.08 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40261 | 131.76 | Potential P4 Event - POI 640226_3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 129.76 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.38 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.49 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.49 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.51 | 508563 PIRKEY 7 345 769761 GEN-2022-139 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.52 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.52 | 507751 RDPOINT4 138 776581 GEN-2023-230 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.52 | 515802 GRACMNT4 138 774981 GEN-2023-150 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.53 | 514801 MINCO 7 345 761250 GEN-2017-233 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.53 | 515543 RENFROW7 345 760809 GEN-2017-203 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.53 | 523267 PRINGLE 6 230 774441 GEN-2023-123 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.53 | 523309 MOORE_CNTY 6 230 772181 GEN-2023-010 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.53 | 655845 GRDNCRK2-MK7 115 655879 OASIS___-MK7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.73 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.73 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.74 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.75 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.75 | 509829 FULTONW4 138 509830 KENSH-E-TP4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.75 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.76 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.76 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.76 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.77 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.79 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.81 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.82 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.82 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.83 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.83 | P12:138:OKGE:BKRBKR176:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.83 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.88 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.88 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.88 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.89 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.9 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.9 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.93 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.93 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.95 | 48983 J1898 SUB 161 3WXFMR J1898 SUB 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.95 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.96 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.96 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.96 | P23:500:EES:PERVIL:R9872 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.96 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.96 | P23:500:EMI:ABF_PRYVL-A | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.98 | 51993 J2199 SUB 345 3WXFMR J2199 SUB 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.99 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.04 | 762779 G18-043 TAP 345 762780 GEN-2018-043 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.07 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.1 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.1 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.1 | P13:NBEC#1 GSU | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.11 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.12 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.18 | P13:SH902T GSU | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.2 | P11:024:DPC:ALMA2:6 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.2 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.21 | P11:18:SPC: BD #6+SSL:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.21 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.21 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.25 | P11:18:SPC: BD #6:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.32 | P12:138:OKGE:BKRBKR130:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.41 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.56 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.59 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.59 | P23:345:XEL:8H14 PRI | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.61 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.64 | GEN-2021-043_POI_650290_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.77 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.77 | P23:345:XEL:8N22 SHC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.78 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.78 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.78 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.81 | 640427 STEELEC9 4.16 640426 STEELEC7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.82 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.85 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.85 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.87 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.93 | P23:345:OPPD:S3740-S3455&CC2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.93 | P41:345:OPPD:S3740-55&CC2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.93 | P42:345:OPPD:S3740-S3455&CC2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.93 | P43:015-345:OPPD:S3740-S3455&CC2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.08 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.1 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.2 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.39 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.42 | P23:345:MEC:CBEC 908 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.43 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.48 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.53 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.58 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.58 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.58 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.58 | Potential P4 Event - POI 640590_10 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.58 | Potential P4 Event - POI 640590_12 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.65 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.71 | Potential P4 Event - POI 645740_6 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.77 | Potential P4 Event - POI 645740_12 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.87 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 134.35 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 134.54 | GEN-2023-224_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 134.54 | Potential P4 Event - POI 640590_9 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 136.42 | Potential P4 Event - POI 645740_5 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 136.86 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40263 | 130.79 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40263 | 130.8 | 512694 CLEVLND7 345 560056 G15066_T 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40263 | 130.98 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40263 | 131.02 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40264 | 130.74 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40264 | 131.07 | P12:345:OKGE:BKRBKR357_1:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40264 | 131.11 | P42:345:OKGE:SB_SOER7383:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40267 | 130.89 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40269 | 130.9 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40269 | 130.97 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40285 | 130.85 | P12:115:HAST:::LINE | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40371 | 131.92 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40426 | 131.24 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40426 | 131.26 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40783 | 132.45 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40783 | 132.57 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40872 | 132.25 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40873 | 133.07 | P12:115:WERE:KNOB-MKEC-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40873 | 133.09 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.42503 | 144.29 | P12:115:WERE:KNOB-NPPD-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45114 | 147.56 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45114 | 149.24 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45114 | 149.25 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.48194 | 164.34 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60884 | 194.13 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60884 | 197.29 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60884 | 197.55 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 771999 G23-222-POI 345 776422 G23-222XFMR1 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 771999 G23-222-POI 345 776425 G23-222XFMR2 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 771999 G23-222-POI 345 776442 G23-223XFMR1 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 776422 G23-222XFMR1 345 776424 G23-222GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 776425 G23-222XFMR2 345 776427 G23-222GEN2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 776442 G23-223XFMR1 345 776444 G23-223GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | GEN-2023-223_POI_771999_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.29875 | 138.37 | GEN-2023-225_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31104 | 137.45 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31135 | 137.65 | Potential P4 Event - POI 640226_4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31142 | 136.7 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.19 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31146 | 136.7 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31147 | 138.54 | P23:345:MEC:CBEC 905 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 136.68 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 136.82 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 136.88 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 136.89 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 136.9 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 136.98 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 137.25 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 137.7 | Potential P4 Event - POI 640226_3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 138.42 | Potential P4 Event - POI 640226_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.23 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.35 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.35 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.38 | 515802 GRACMNT4 138 774981 GEN-2023-150 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.39 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.39 | 515543 RENFROW7 345 760809 GEN-2017-203 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.4 | 514801 MINCO 7 345 761250 GEN-2017-233 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.4 | 523267 PRINGLE 6 230 774441 GEN-2023-123 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.4 | 523309 MOORE_CNTY 6 230 772181 GEN-2023-010 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.4 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.4 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.41 | 655846 F9______-MK7 115 655872 G9TAP___-MK7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.61 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.61 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.61 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.61 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.62 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.63 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.63 | 509829 FULTONW4 138 509830 KENSH-E-TP4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.63 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.64 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.65 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.65 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.65 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.67 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.69 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.7 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.71 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.71 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.71 | P12:138:OKGE:BKRBKR176:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.71 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.71 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.77 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.77 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.77 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.78 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.79 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.79 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.83 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.83 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.84 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.85 | 48983 J1898 SUB 161 3WXFMR J1898 SUB 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.85 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.85 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.85 | P23:500:EES:PERVIL:R9872 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.85 | P23:500:EMI:ABF_PRYVL-A | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.86 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.88 | 51993 J2199 SUB 345 3WXFMR J2199 SUB 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.89 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.89 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.94 | 762779 G18-043 TAP 345 762780 GEN-2018-043 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.97 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137 | P13:NBEC#1 GSU | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.01 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.01 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.01 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.02 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.09 | P13:SH902T GSU | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.11 | P11:024:DPC:ALMA2:6 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.11 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.12 | P11:18:SPC: BD #6+SSL:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.12 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.12 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.17 | P11:18:SPC: BD #6:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.23 | P12:138:OKGE:BKRBKR130:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.33 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.5 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.52 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.53 | P23:345:XEL:8H14 PRI | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.55 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.58 | GEN-2021-043_POI_650290_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.72 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.72 | P23:345:XEL:8N22 SHC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.73 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.73 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.73 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.77 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.8 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.8 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.83 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.87 | P23:345:OPPD:S3740-S3455&CC2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.87 | P41:345:OPPD:S3740-55&CC2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.87 | P42:345:OPPD:S3740-S3455&CC2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.87 | P43:015-345:OPPD:S3740-S3455&CC2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.05 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.07 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.17 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.37 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.41 | P23:345:MEC:CBEC 908 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.42 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.48 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.52 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.58 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.58 | Potential P4 Event - POI 640590_10 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.58 | Potential P4 Event - POI 640590_11 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.59 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.59 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.65 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.7 | Potential P4 Event - POI 645740_6 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.78 | Potential P4 Event - POI 645740_12 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.88 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 140.43 | 640112 CLATONA9 34.5 3WXFMR CLATONIA T1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 140.47 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 140.67 | GEN-2023-224_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 140.67 | Potential P4 Event - POI 640590_9 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 142.67 | Potential P4 Event - POI 645740_5 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 143.13 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3115 | 136.68 | 512694 CLEVLND7 345 560056 G15066_T 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3115 | 136.68 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3115 | 136.88 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3115 | 136.92 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31151 | 136.62 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31151 | 136.97 | P12:345:OKGE:BKRBKR357_1:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31151 | 137.01 | P42:345:OKGE:SB_SOER7383:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31153 | 136.78 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31154 | 136.79 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31154 | 136.87 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31167 | 136.74 | P12:115:HAST:::LINE | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31233 | 137.88 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31276 | 137.15 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31276 | 137.17 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31552 | 138.44 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31552 | 138.57 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31621 | 138.23 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31621 | 139.1 | P12:115:WERE:KNOB-MKEC-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31621 | 139.12 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.32883 | 151.05 | P12:115:WERE:KNOB-NPPD-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34903 | 154.53 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34903 | 154.53 | P13:115-161:NPPD:HUMBOLT5:T2::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34903 | 155.88 | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34903 | 156.33 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34903 | 156.34 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.37286 | 172.43 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.55406 | 246.37 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.11579 | 106.34 | P12:115:WERE:KNOB-NPPD-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.11708 | 109.72 | 640208 HARBINE7 115 640426 STEELEC7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.13059 | 102.3 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.13059 | 103.49 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.13059 | 103.53 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.14955 | 115.73 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640234 HUMBOLT5 161 996842 HUMBOLDT T2 115 1 | 126 | 126 | 0.17938 | 100.58 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | 121 | 121 | 0.17938 | 102.4 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 640278 SHELDON7 115 650246 SW7&BENNET7 115 1 | 240 | 240 | 0.14723 | 102.74 | Potential P4 Event - POI 640590_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 771999 G23-222-POI 345 776422 G23-222XFMR1 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 771999 G23-222-POI 345 776425 G23-222XFMR2 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 771999 G23-222-POI 345 776442 G23-223XFMR1 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 776422 G23-222XFMR1 345 776424 G23-222GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 776425 G23-222XFMR2 345 776427 G23-222GEN2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 776442 G23-223XFMR1 345 776444 G23-223GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | GEN-2023-223_POI_771999_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | 193 | 193 | 0.27216 | 140.8 | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 193 | 193 | 0.22811 | 101.78 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 193 | 193 | 0.27331 | 141.4 | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.16843 | 149.47 | P13:115-230:SUNC:CONCORDIA_XFR:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17125 | 144.07 | 539805 ELMCREEK7 345 3WXFMR ELMCREEK T1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17194 | 143.74 | 532765 HOYT 7 345 3WXFMR HOYT1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1721 | 143.82 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17212 | 143.37 | P42:345:OKGE:SB_RARD7381:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17212 | 145.56 | Potential P4 Event - POI 515576_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 141.87 | P13:69-161:XEL:AUTO-SINGLE:WBYRON8:BYRON5:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 141.95 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 141.95 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.03 | P12:115:XEL:AUTO-SINGLE:NSSTAP7:NSSTL7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.03 | P21:115:XEL:AUTO-SINGLE:NSSTAP7:NSSTL7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.08 | P12:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.08 | P21:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.12 | P21:115:XEL:AUTO-SINGLE:REDROCK7:NSSJCT7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.14 | 506944 CHAMSPR5 161 776241 GEN-2023-213 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.15 | 512635 KERR GR5 161 773081 GEN-2023-055 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.15 | 528013 PHANTOM 3 115 775661 GEN-2023-184 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.15 | P12:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.16 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.19 | 508298 LYDIA 7 345 764075 GEN-2020-054 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.21 | P12:345:XEL:ASK-ECL SPS | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.22 | 505522 VAN BUR5 161 773101 GEN-2023-056 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.23 | 526936 YOAKUM 7 345 766120 GEN-2021-090 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.24 | 515235 PECANCK7 345 762823 GEN-2018-048 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.24 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.25 | 659387 KUMMERDG-BE3 345 659390 PATENTGT-BE3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.28 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.31 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.36 | 509782 R.S.S.-7 345 588040 G16133G16146 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.38 | 300024 1CHOTST6 16.0 301348 5CHOTEAU2 161 20 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.38 | 300031 1CHOTST3 16.0 300069 5CHOTEAU1 161 10 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.4 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.5 | 512749 PAWNSW4 138 773121 GEN-2023-057 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.6 | P13:161-22:AEPW:FLINTCR5:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.68 | 514922 CLASSEN4 138 775341 GEN-2023-168 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.73 | 640112 CLATONA9 34.5 3WXFMR CLATONIA T1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.75 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.77 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.77 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.77 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.81 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.81 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.83 | P13:345:GRDA:GRDA2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.85 | P12:161:GRDA:SALINA 5-SALNCRK5:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.86 | 560053 G15052_T 345 562900 G15052_1 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.88 | P13:138-24:AEPW:TURK 4:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.9 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.91 | P13:345-22:AEPW:N.E.S.-7_#1:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.98 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 142.99 | P23:500:EES-EAI:WH_BLF:B7942 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.02 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.03 | P23:345:AEPW:NES CB 3417B NBTB:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.06 | P23:345:AEPW:NES CB 3413B NBTB:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.06 | P41:345:AEPW:NES CB 3413B NBTB+FAULT:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.08 | 515156 WASHPRK4 138 775321 GEN-2023-167 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.13 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.28 | 776061 GEN-2023-204 345 776064 G23-204GEN1 23.5 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.38 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.39 | 525481 PLANT_X 6 230 774821 GEN-2023-142 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.4 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.41 | 532793 NEOSHO 7 345 772981 GEN-2023-050 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.5 | 532766 JEC N 7 345 766240 GEN-2021-107 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.52 | 515852 DGRASSE7 345 773981 GEN-2023-100 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.55 | 527000 GAINES_PLNT7 345 527020 SIDEWINDER 7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.59 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.63 | P13:115:WERE:EMAN-TX-3-230-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.64 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.87 | P11:HV:EES::1RVR_BND_G1!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.87 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.87 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.87 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.91 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.96 | 525832 TUCO_INT 7 345 525850 ELK_CT1 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.96 | 525832 TUCO_INT 7 345 769921 GEN-2022-147 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 143.97 | 515800 GRACMNT7 345 775261 GEN-2023-164 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 144 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 144.11 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 144.11 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 144.12 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 144.15 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 144.21 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 144.24 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 144.24 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 144.31 | 515852 DGRASSE7 345 776821 GEN-2023-102 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 144.31 | GEN-2023-102_POI_515852_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 144.34 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 144.34 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 144.88 | 776060 G23-204-TAP 345 776061 GEN-2023-204 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 144.89 | GEN-2023-204_POI_776060_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 144.97 | Potential P4 Event - POI 515576_20 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 145.13 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 146.22 | 640218 HEBRN N7 115 640012 HEBRON G 13.8 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 146.26 | Potential P4 Event - POI 525832_3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 147.62 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 149.29 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 161.56 | 640208 HARBINE7 115 772201 GEN-2023-011 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 161.56 | 772201 GEN-2023-011 115 772202 G23-011XFMR1 34.5 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17214 | 161.56 | GEN-2023-011_POI_640208_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 141.89 | 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 141.91 | 338120 5S.LEAD HILL 161 505461 BULL SH W5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 142.23 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:HCKRYCK3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 142.29 | P23:345:ITCM:HAZLTON3 9985:IA-NE | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 142.32 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 142.36 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 149.33 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17216 | 142.13 | P12:345:XEL:AUTO-SINGLE:WILMART3:SHEASLK3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17216 | 142.61 | P23:345:AEPW:VALLIANT CB 3421A NBTB:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17216 | 142.98 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 143.69 | P42:500:OKGE:SB_FTTH8581:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 143.69 | P42:500:OKGE:SB_FTTH8585:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 143.71 | P12:500:OKGE-EESAR:OKGE-EESEAI:BKRBKR317::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 143.71 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17221 | 142.62 | 300041 7FRANKS 345 300051 7FRANKSRCTP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17221 | 142.63 | 300042 7HUBEN 345 300051 7FRANKSRCTP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17223 | 142.55 | 635580 ARBOR HILL 3 345 635590 FALLOW AVE 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17223 | 142.93 | 635580 ARBOR HILL 3 345 635622 RCCN TRL 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1723 | 143.89 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1723 | 143.89 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1723 | 143.92 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17235 | 142.43 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17235 | 142.64 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17235 | 142.64 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17235 | 142.64 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17235 | 142.64 | P23:345:MEC:BONDURANT 906 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17235 | 142.64 | P23:345:MEC:BONDURANT:903::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17235 | 142.64 | P23:345:MEC:BONDURANT:906::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17235 | 143.04 | P23:345:MEC:MONTEZUMA:902::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17259 | 143.99 | 300039 7FAIRPT 345 640139 COOPER 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17273 | 144.44 | 541197 MULLNCR7 345 771140 G22-208-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17273 | 144.44 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS_1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17273 | 144.48 | 541197 MULLNCR7 345 541510 HOLT 7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17277 | 146.26 | Potential P4 Event - POI 532772_9 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17298 | 149.99 | 532913 KELLY 5 161 3WXFMR KELL TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.173 | 145.52 | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1732 | 146.09 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1732 | 146.09 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17497 | 152.69 | P12:161:WERE:TECH-KELL-OPPD-161:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17497 | 152.69 | P12:161:WERE-OPPD:S1399-KELLY:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17513 | 146.93 | Potential P4 Event - POI 640271_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17672 | 152.06 | P21:161:OPPD:S1399-KELLY:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17766 | 152.52 | Potential P4 Event - POI 640590_7 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17766 | 152.52 | Potential P4 Event - POI 640590_8 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17929 | 147.26 | Potential P4 Event - POI 640271_1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.18703 | 166.39 | Potential P4 Event - POI 640590_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.19983 | 159.5 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.19983 | 161.27 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.23425 | 177.76 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.23425 | 179.69 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.23425 | 179.94 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.26657 | 200.2 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640361 STEINER7 115 1 | 121 | 121 | 0.17938 | 104.23 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.29875 | 141.91 | GEN-2023-225_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31104 | 141 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31135 | 141.21 | Potential P4 Event - POI 640226_4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31142 | 140.27 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.75 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31146 | 140.26 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31147 | 142.07 | P23:345:MEC:CBEC 905 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 140.24 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 140.38 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 140.44 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 140.45 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 140.46 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 140.54 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 140.8 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 141.25 | Potential P4 Event - POI 640226_3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 141.96 | Potential P4 Event - POI 640226_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.81 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.92 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.92 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.95 | 515802 GRACMNT4 138 774981 GEN-2023-150 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.96 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.96 | 515543 RENFROW7 345 760809 GEN-2017-203 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.96 | 655845 GRDNCRK2-MK7 115 655879 OASIS___-MK7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.97 | 514801 MINCO 7 345 761250 GEN-2017-233 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.97 | 523267 PRINGLE 6 230 774441 GEN-2023-123 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.97 | 523309 MOORE_CNTY 6 230 772181 GEN-2023-010 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.97 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 139.97 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.18 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.18 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.18 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.18 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.19 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.19 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.2 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.2 | 509829 FULTONW4 138 509830 KENSH-E-TP4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.21 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.21 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.21 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.22 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.24 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.25 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.26 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.27 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.27 | P12:138:OKGE:BKRBKR176:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.27 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.28 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.28 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.33 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.34 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.34 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.34 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.35 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.35 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.39 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.39 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.4 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.41 | 48983 J1898 SUB 161 3WXFMR J1898 SUB 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.41 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.41 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.41 | P23:500:EES:PERVIL:R9872 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.41 | P23:500:EMI:ABF_PRYVL-A | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.42 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.44 | 51993 J2199 SUB 345 3WXFMR J2199 SUB 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.45 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.45 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.5 | 762779 G18-043 TAP 345 762780 GEN-2018-043 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.53 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.56 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.56 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.56 | P13:NBEC#1 GSU | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.57 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.58 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.64 | P13:SH902T GSU | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.67 | P11:024:DPC:ALMA2:6 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.67 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.67 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.67 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.68 | P11:18:SPC: BD #6+SSL:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.72 | P11:18:SPC: BD #6:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.79 | P12:138:OKGE:BKRBKR130:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 140.88 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.05 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.07 | P23:345:XEL:8H14 PRI | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.08 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.09 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.13 | GEN-2021-043_POI_650290_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.26 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.27 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.27 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.27 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.27 | P23:345:XEL:8N22 SHC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.3 | 640427 STEELEC9 4.16 640426 STEELEC7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.31 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.35 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.35 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.37 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.45 | P23:345:OPPD:S3740-S3455&CC2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.45 | P41:345:OPPD:S3740-55&CC2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.45 | P42:345:OPPD:S3740-S3455&CC2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.45 | P43:015-345:OPPD:S3740-S3455&CC2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.59 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.61 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.71 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.91 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.94 | P23:345:MEC:CBEC 908 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.95 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.01 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.05 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.11 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.11 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.11 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.11 | Potential P4 Event - POI 640590_12 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.11 | Potential P4 Event - POI 640590_13 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.18 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.26 | Potential P4 Event - POI 645740_6 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.3 | Potential P4 Event - POI 645740_12 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 142.41 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 143.96 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 144.16 | GEN-2023-224_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 144.16 | Potential P4 Event - POI 640590_9 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 146.12 | Potential P4 Event - POI 645740_5 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 146.58 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3115 | 140.24 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3115 | 140.25 | 512694 CLEVLND7 345 560056 G15066_T 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3115 | 140.44 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3115 | 140.48 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31151 | 140.18 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31151 | 140.53 | P12:345:OKGE:BKRBKR357_1:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31151 | 140.57 | P42:345:OKGE:SB_SOER7383:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31153 | 140.34 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31154 | 140.35 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31154 | 140.43 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31167 | 140.3 | P12:115:HAST:::LINE | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31233 | 141.42 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31276 | 140.7 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31276 | 140.72 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31552 | 141.97 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31552 | 142.1 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31621 | 141.76 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31621 | 142.62 | P12:115:WERE:KNOB-MKEC-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31621 | 142.64 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.32883 | 154.35 | P12:115:WERE:KNOB-NPPD-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34903 | 157.75 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34903 | 157.75 | P13:115-161:NPPD:HUMBOLT5:T2::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34903 | 159.08 | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34903 | 159.51 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34903 | 159.53 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.37286 | 175.27 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.55406 | 247.71 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.38615 | 132.39 | GEN-2023-225_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40204 | 131.52 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40244 | 131.71 | Potential P4 Event - POI 640226_4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40253 | 130.82 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40257 | 130.81 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40257 | 131.28 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40259 | 132.54 | P23:345:MEC:CBEC 905 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4026 | 131.01 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4026 | 131.33 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4026 | 132.43 | Potential P4 Event - POI 640226_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40261 | 130.79 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40261 | 130.81 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40261 | 130.93 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40261 | 130.99 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40261 | 130.99 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40261 | 131.08 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40261 | 131.76 | Potential P4 Event - POI 640226_3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 129.76 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.38 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.49 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.49 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.51 | 508563 PIRKEY 7 345 769761 GEN-2022-139 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.52 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.52 | 507751 RDPOINT4 138 776581 GEN-2023-230 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.52 | 515802 GRACMNT4 138 774981 GEN-2023-150 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.53 | 514801 MINCO 7 345 761250 GEN-2017-233 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.53 | 515543 RENFROW7 345 760809 GEN-2017-203 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.53 | 523267 PRINGLE 6 230 774441 GEN-2023-123 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.53 | 523309 MOORE_CNTY 6 230 772181 GEN-2023-010 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.53 | 655845 GRDNCRK2-MK7 115 655879 OASIS___-MK7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.73 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.73 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.74 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.75 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.75 | 509829 FULTONW4 138 509830 KENSH-E-TP4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.75 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.76 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.76 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.76 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.77 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.79 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.81 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.82 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.82 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.83 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.83 | P12:138:OKGE:BKRBKR176:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.83 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.88 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.88 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.88 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.89 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.9 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.9 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.93 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.93 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.95 | 48983 J1898 SUB 161 3WXFMR J1898 SUB 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.95 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.96 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.96 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.96 | P23:500:EES:PERVIL:R9872 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.96 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.96 | P23:500:EMI:ABF_PRYVL-A | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.98 | 51993 J2199 SUB 345 3WXFMR J2199 SUB 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 130.99 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.04 | 762779 G18-043 TAP 345 762780 GEN-2018-043 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.07 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.1 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.1 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.1 | P13:NBEC#1 GSU | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.11 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.12 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.18 | P13:SH902T GSU | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.2 | P11:024:DPC:ALMA2:6 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.2 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.21 | P11:18:SPC: BD #6+SSL:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.21 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.21 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.25 | P11:18:SPC: BD #6:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.32 | P12:138:OKGE:BKRBKR130:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.41 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.56 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.59 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.59 | P23:345:XEL:8H14 PRI | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.61 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.64 | GEN-2021-043_POI_650290_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.77 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.77 | P23:345:XEL:8N22 SHC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.78 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.78 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.78 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.81 | 640427 STEELEC9 4.16 640426 STEELEC7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.82 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.85 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.85 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.87 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.93 | P23:345:OPPD:S3740-S3455&CC2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.93 | P41:345:OPPD:S3740-55&CC2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.93 | P42:345:OPPD:S3740-S3455&CC2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.93 | P43:015-345:OPPD:S3740-S3455&CC2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.08 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.1 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.2 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.39 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.42 | P23:345:MEC:CBEC 908 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.43 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.48 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.53 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.58 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.58 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.58 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.58 | Potential P4 Event - POI 640590_10 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.58 | Potential P4 Event - POI 640590_12 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.65 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.71 | Potential P4 Event - POI 645740_6 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.77 | Potential P4 Event - POI 645740_12 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 132.87 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 134.35 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 134.54 | GEN-2023-224_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 134.54 | Potential P4 Event - POI 640590_9 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 136.42 | Potential P4 Event - POI 645740_5 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 136.86 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40263 | 130.79 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40263 | 130.8 | 512694 CLEVLND7 345 560056 G15066_T 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40263 | 130.98 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40263 | 131.02 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40264 | 130.74 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40264 | 131.07 | P12:345:OKGE:BKRBKR357_1:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40264 | 131.11 | P42:345:OKGE:SB_SOER7383:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40267 | 130.89 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40269 | 130.9 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40269 | 130.97 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40285 | 130.85 | P12:115:HAST:::LINE | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40371 | 131.92 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40426 | 131.24 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40426 | 131.26 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40783 | 132.45 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40783 | 132.57 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40872 | 132.25 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40873 | 133.07 | P12:115:WERE:KNOB-MKEC-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40873 | 133.09 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.42503 | 144.29 | P12:115:WERE:KNOB-NPPD-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45114 | 147.56 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45114 | 149.24 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45114 | 149.25 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.48194 | 164.34 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60884 | 194.13 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60884 | 197.29 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60884 | 197.55 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 771999 G23-222-POI 345 776422 G23-222XFMR1 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 771999 G23-222-POI 345 776425 G23-222XFMR2 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 776422 G23-222XFMR1 345 776424 G23-222GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 776425 G23-222XFMR2 345 776427 G23-222GEN2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.29875 | 138.37 | GEN-2023-225_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31104 | 137.45 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31135 | 137.65 | Potential P4 Event - POI 640226_4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31142 | 136.7 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.19 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31146 | 136.7 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31147 | 138.54 | P23:345:MEC:CBEC 905 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 136.68 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 136.82 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 136.88 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 136.89 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 136.9 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 136.98 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 137.25 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 137.7 | Potential P4 Event - POI 640226_3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 138.42 | Potential P4 Event - POI 640226_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.23 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.35 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.35 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.38 | 515802 GRACMNT4 138 774981 GEN-2023-150 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.39 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.39 | 515543 RENFROW7 345 760809 GEN-2017-203 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.4 | 514801 MINCO 7 345 761250 GEN-2017-233 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.4 | 523267 PRINGLE 6 230 774441 GEN-2023-123 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.4 | 523309 MOORE_CNTY 6 230 772181 GEN-2023-010 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.4 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.4 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.41 | 655846 F9______-MK7 115 655872 G9TAP___-MK7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.61 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.61 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.61 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.61 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.62 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.63 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.63 | 509829 FULTONW4 138 509830 KENSH-E-TP4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.63 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.64 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.65 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.65 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.65 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.67 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.69 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.7 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.71 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.71 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.71 | P12:138:OKGE:BKRBKR176:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.71 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.71 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.77 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.77 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.77 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.78 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.79 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.79 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.83 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.83 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.84 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.85 | 48983 J1898 SUB 161 3WXFMR J1898 SUB 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.85 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.85 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.85 | P23:500:EES:PERVIL:R9872 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.85 | P23:500:EMI:ABF_PRYVL-A | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.86 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.88 | 51993 J2199 SUB 345 3WXFMR J2199 SUB 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.89 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.89 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.94 | 762779 G18-043 TAP 345 762780 GEN-2018-043 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 136.97 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137 | P13:NBEC#1 GSU | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.01 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.01 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.01 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.02 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.09 | P13:SH902T GSU | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.11 | P11:024:DPC:ALMA2:6 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.11 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.12 | P11:18:SPC: BD #6+SSL:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.12 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.12 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.17 | P11:18:SPC: BD #6:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.23 | P12:138:OKGE:BKRBKR130:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.33 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.5 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.52 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.53 | P23:345:XEL:8H14 PRI | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.55 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.58 | GEN-2021-043_POI_650290_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.72 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.72 | P23:345:XEL:8N22 SHC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.73 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.73 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.73 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.77 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.8 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.8 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.83 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.87 | P23:345:OPPD:S3740-S3455&CC2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.87 | P41:345:OPPD:S3740-55&CC2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.87 | P42:345:OPPD:S3740-S3455&CC2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.87 | P43:015-345:OPPD:S3740-S3455&CC2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.05 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.07 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.17 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.37 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.41 | P23:345:MEC:CBEC 908 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.42 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.48 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.52 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.58 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.58 | Potential P4 Event - POI 640590_10 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.58 | Potential P4 Event - POI 640590_11 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.59 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.59 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.65 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.7 | Potential P4 Event - POI 645740_6 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.78 | Potential P4 Event - POI 645740_12 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 138.88 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 140.43 | 640112 CLATONA9 34.5 3WXFMR CLATONIA T1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 140.47 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 140.67 | GEN-2023-224_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 140.67 | Potential P4 Event - POI 640590_9 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 142.67 | Potential P4 Event - POI 645740_5 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 143.13 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3115 | 136.68 | 512694 CLEVLND7 345 560056 G15066_T 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3115 | 136.68 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3115 | 136.88 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3115 | 136.92 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31151 | 136.62 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31151 | 136.97 | P12:345:OKGE:BKRBKR357_1:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31151 | 137.01 | P42:345:OKGE:SB_SOER7383:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31153 | 136.78 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31154 | 136.79 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31154 | 136.87 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31167 | 136.74 | P12:115:HAST:::LINE | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31233 | 137.88 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31276 | 137.15 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31276 | 137.17 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31552 | 138.44 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31552 | 138.57 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31621 | 138.23 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31621 | 139.1 | P12:115:WERE:KNOB-MKEC-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31621 | 139.12 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.32883 | 151.05 | P12:115:WERE:KNOB-NPPD-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34903 | 154.53 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34903 | 154.53 | P13:115-161:NPPD:HUMBOLT5:T2::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34903 | 155.88 | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34903 | 156.33 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34903 | 156.34 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.37286 | 172.43 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.55406 | 246.37 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.11579 | 106.34 | P12:115:WERE:KNOB-NPPD-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.11708 | 109.72 | 640208 HARBINE7 115 640426 STEELEC7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.13059 | 102.3 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.13059 | 103.49 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.13059 | 103.53 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.14955 | 115.73 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640234 HUMBOLT5 161 996842 HUMBOLDT T2 115 1 | 126 | 126 | 0.17938 | 100.58 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | 121 | 121 | 0.17938 | 102.4 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 640278 SHELDON7 115 650246 SW7&BENNET7 115 1 | 240 | 240 | 0.14723 | 102.74 | Potential P4 Event - POI 640590_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 771999 G23-222-POI 345 776422 G23-222XFMR1 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 771999 G23-222-POI 345 776425 G23-222XFMR2 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 776422 G23-222XFMR1 345 776424 G23-222GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996911 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 776425 G23-222XFMR2 345 776427 G23-222GEN2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-224 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.05946 | 166.39 | Potential P4 Event - POI 640590_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-224 | FROM->TO | 640278 SHELDON7 115 650246 SW7&BENNET7 115 1 | 240 | 240 | 0.18962 | 102.74 | Potential P4 Event - POI 640590_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-225 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.05946 | 166.39 | Potential P4 Event - POI 640590_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 24SP | GEN-2023-225 | FROM->TO | 640278 SHELDON7 115 650246 SW7&BENNET7 115 1 | 240 | 240 | 0.18962 | 102.74 | Potential P4 Event - POI 640590_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-059 | FROM->TO | 547469 RIV4525 161 547498 STL439 5 161 1 | 461 | 461 | 0.06708 | 100.35 | 547467 ORO110 5 161 547469 RIV4525 161 1 | Cumulative Impact | RIV4525 to STL439 Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-062 | FROM->TO | 547469 RIV4525 161 547498 STL439 5 161 1 | 461 | 461 | 0.06888 | 100.35 | 547467 ORO110 5 161 547469 RIV4525 161 1 | Cumulative Impact | RIV4525 to STL439 Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-077 | FROM->TO | 547469 RIV4525 161 547498 STL439 5 161 1 | 461 | 461 | 0.07186 | 100.35 | 547467 ORO110 5 161 547469 RIV4525 161 1 | Cumulative Impact | RIV4525 to STL439 Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60581 | 103.06 | Potential P4 Event - POI 645740_4 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60581 | 106.7 | 645454 S3454 3 345 645740 S3740 3 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.66 | Potential P4 Event - POI 645740_1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-077 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 156.79 | Potential P4 Event - POI 645740_0 | Cumulative Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-078 | FROM->TO | 547469 RIV4525 161 547498 STL439 5 161 1 | 461 | 461 | 0.07186 | 100.35 | 547467 ORO110 5 161 547469 RIV4525 161 1 | Cumulative Impact | RIV4525 to STL439 Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60581 | 103.06 | Potential P4 Event - POI 645740_4 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60581 | 106.7 | 645454 S3454 3 345 645740 S3740 3 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.66 | Potential P4 Event - POI 645740_1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-078 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 156.79 | Potential P4 Event - POI 645740_0 | Cumulative Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-079 | FROM->TO | 547469 RIV4525 161 547498 STL439 5 161 1 | 461 | 461 | 0.07186 | 100.35 | 547467 ORO110 5 161 547469 RIV4525 161 1 | Cumulative Impact | RIV4525 to STL439 Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60581 | 103.06 | Potential P4 Event - POI 645740_4 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.60581 | 106.7 | 645454 S3454 3 345 645740 S3740 3 345 1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 0.99995 | 140.66 | Potential P4 Event - POI 645740_1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-079 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 0.99995 | 156.79 | Potential P4 Event - POI 645740_0 | Cumulative Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-183 | FROM->TO | 547469 RIV4525 161 547498 STL439 5 161 1 | 461 | 461 | 0.08304 | 100.35 | 547467 ORO110 5 161 547469 RIV4525 161 1 | Cumulative Impact | RIV4525 to STL439 Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-204 | FROM->TO | 547469 RIV4525 161 547498 STL439 5 161 1 | 461 | 461 | 0.06981 | 100.35 | 547467 ORO110 5 161 547469 RIV4525 161 1 | Cumulative Impact | RIV4525 to STL439 Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 547469 RIV4525 161 547498 STL439 5 161 1 | 461 | 461 | 0.07367 | 100.35 | 547467 ORO110 5 161 547469 RIV4525 161 1 | Cumulative Impact | RIV4525 to STL439 Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | 193 | 193 | 0.27226 | 139.25 | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 193 | 193 | 0.22818 | 101.08 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 193 | 193 | 0.27341 | 139.83 | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.16844 | 147.89 | P13:115-230:SUNC:CONCORDIA_XFR:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17129 | 141.92 | 539805 ELMCREEK7 345 3WXFMR ELMCREEK T1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17199 | 141.52 | 532765 HOYT 7 345 3WXFMR HOYT1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 141.55 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17218 | 141.03 | P42:345:OKGE:SB_RARD7381:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17218 | 141.51 | P13:115:WERE:EMAN-TX-3-230-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17218 | 143.19 | Potential P4 Event - POI 515576_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.6 | P13:69-161:XEL:AUTO-SINGLE:WBYRON8:BYRON5:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.64 | 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.68 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.68 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.77 | P12:115:XEL:AUTO-SINGLE:NSSTAP7:NSSTL7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.77 | P21:115:XEL:AUTO-SINGLE:NSSTAP7:NSSTL7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.82 | P12:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.82 | P21:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.84 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.86 | P21:115:XEL:AUTO-SINGLE:REDROCK7:NSSJCT7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.88 | P12:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.89 | 506944 CHAMSPR5 161 776241 GEN-2023-213 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.89 | 512635 KERR GR5 161 773081 GEN-2023-055 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.89 | 528013 PHANTOM 3 115 775661 GEN-2023-184 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.92 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.93 | 508298 LYDIA 7 345 764075 GEN-2020-054 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.93 | P12:345:XEL:ASK-ECL SPS | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.96 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.97 | 505522 VAN BUR5 161 773101 GEN-2023-056 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.99 | 526936 YOAKUM 7 345 766120 GEN-2021-090 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.01 | 515235 PECANCK7 345 762823 GEN-2018-048 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.03 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.04 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.05 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.12 | 640230 HOSK.T89 34.5 640227 HOSKINS4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.15 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.15 | 509782 R.S.S.-7 345 588040 G16133G16146 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.22 | P12:138:AEPW:ARSHILL4:STLGENS4::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.24 | 512749 PAWNSW4 138 773121 GEN-2023-057 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.29 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.31 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.37 | P13:161-22:AEPW:FLINTCR5:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.41 | 514922 CLASSEN4 138 775341 GEN-2023-168 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.46 | 640112 CLATONA9 34.5 3WXFMR CLATONIA T1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.5 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.53 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.53 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.54 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.56 | 560053 G15052_T 345 562900 G15052_1 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.56 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.57 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.58 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.6 | P11:345:GRDA:GRDA17-1:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.61 | P13:345:GRDA:GRDA2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.61 | P41:345:GRDA:GRDA CB320:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.63 | P12:161:GRDA:SALINA 5-SALNCRK5:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.63 | P13:138-24:AEPW:TURK 4:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.66 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.74 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.75 | P23:500:EES-EAI:WH_BLF:B7942 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.79 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.82 | 515156 WASHPRK4 138 775321 GEN-2023-167 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.03 | 776061 GEN-2023-204 345 776067 G23-204GEN2 23.5 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.13 | 525481 PLANT_X 6 230 774821 GEN-2023-142 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.13 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.18 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.2 | 532793 NEOSHO 7 345 772981 GEN-2023-050 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.22 | 532766 JEC N 7 345 766240 GEN-2021-107 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.23 | 515852 DGRASSE7 345 773981 GEN-2023-100 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.32 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.4 | 527000 GAINES_PLNT7 345 527020 SIDEWINDER 7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.65 | P11:HV:EES::1RVR_BND_G1!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.65 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.65 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.65 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.69 | 525832 TUCO_INT 7 345 525850 ELK_CT1 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.69 | 525832 TUCO_INT 7 345 769921 GEN-2022-147 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.7 | 515800 GRACMNT7 345 775261 GEN-2023-164 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.71 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.8 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.89 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.89 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.89 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.9 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.9 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 142 | 515852 DGRASSE7 345 776821 GEN-2023-102 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 142.01 | GEN-2023-102_POI_515852_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 142.05 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 142.05 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 142.15 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 142.15 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 142.63 | Potential P4 Event - POI 515576_20 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 142.65 | 776060 G23-204-TAP 345 776061 GEN-2023-204 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 142.65 | GEN-2023-204_POI_776060_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 142.85 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 143.78 | 640218 HEBRN N7 115 640012 HEBRON G 13.8 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 144 | Potential P4 Event - POI 525832_3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 145.41 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 146.54 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 159.59 | 640208 HARBINE7 115 772201 GEN-2023-011 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 159.59 | 772201 GEN-2023-011 115 772202 G23-011XFMR1 34.5 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 159.59 | GEN-2023-011_POI_640208_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1722 | 139.64 | 659425 SD.LS-KS-MB3 345 763666 G21-037-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1722 | 139.66 | 338120 5S.LEAD HILL 161 505461 BULL SH W5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1722 | 139.96 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:HCKRYCK3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1722 | 140.02 | P23:345:ITCM:HAZLTON3 9985:IA-NE | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1722 | 140.04 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1722 | 140.09 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1722 | 146.61 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17221 | 139.89 | P12:345:XEL:AUTO-SINGLE:WILMART3:SHEASLK3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17221 | 140.43 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17221 | 140.67 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17224 | 141.48 | P42:500:OKGE:SB_FTTH8581:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17224 | 141.48 | P42:500:OKGE:SB_FTTH8585:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17224 | 141.5 | P12:500:OKGE-EESAR:OKGE-EESEAI:BKRBKR317::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17224 | 141.5 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17226 | 140.25 | 300041 7FRANKS 345 300051 7FRANKSRCTP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17226 | 140.25 | 300042 7HUBEN 345 300051 7FRANKSRCTP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17228 | 140.27 | 635580 ARBOR HILL 3 345 635590 FALLOW AVE 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17228 | 140.67 | 635580 ARBOR HILL 3 345 635622 RCCN TRL 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17234 | 141.33 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17234 | 141.33 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17234 | 141.37 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1724 | 140.04 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1724 | 140.26 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1724 | 140.26 | P23:345:MEC:BONDURANT:906::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1724 | 140.27 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1724 | 140.27 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1724 | 140.69 | P23:345:MEC:MONTEZUMA:902::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17264 | 141.45 | 300039 7FAIRPT 345 640139 COOPER 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1728 | 141.65 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1728 | 141.66 | 541197 MULLNCR7 345 771140 G22-208-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1728 | 141.67 | 541197 MULLNCR7 345 541510 HOLT 7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17281 | 143.51 | Potential P4 Event - POI 532772_9 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17306 | 147.03 | 532913 KELLY 5 161 3WXFMR KELL TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17307 | 142.71 | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17328 | 143.11 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17328 | 143.11 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17506 | 149.4 | P12:161:WERE:TECH-KELL-OPPD-161:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17506 | 149.4 | P12:161:WERE-OPPD:S1399-KELLY:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17512 | 144.65 | Potential P4 Event - POI 640271_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17682 | 148.72 | P21:161:OPPD:S1399-KELLY:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17768 | 150.29 | Potential P4 Event - POI 640590_7 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17768 | 150.29 | Potential P4 Event - POI 640590_8 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17924 | 145.49 | Potential P4 Event - POI 640271_1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.187 | 164 | Potential P4 Event - POI 640590_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.19987 | 156.79 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.19987 | 158.58 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.2343 | 175.6 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.2343 | 177.52 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.2343 | 177.77 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.26662 | 198.16 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640361 STEINER7 115 1 | 121 | 121 | 0.17946 | 103.33 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.29874 | 142.9 | GEN-2023-225_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.311 | 142.19 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31131 | 142.19 | Potential P4 Event - POI 640226_4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3114 | 141.82 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31141 | 141.33 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31142 | 143.08 | P23:345:MEC:CBEC 905 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31143 | 141.27 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31143 | 141.46 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31143 | 141.84 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31143 | 142.27 | Potential P4 Event - POI 640226_3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31143 | 142.94 | Potential P4 Event - POI 640226_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 140.99 | 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 140.99 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.19 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.19 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.21 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.22 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.22 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.23 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.23 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.28 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.28 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.29 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.3 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.3 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.35 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.35 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.36 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.36 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.39 | 541198 PECULR 7 345 541200 PHILL 7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.42 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.42 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.43 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.43 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.43 | P23:500:EES:PERVIL:R9872 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.43 | P23:500:EMI:ABF_PRYVL-A | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.44 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.47 | P41:345:OPPD:S3740-55&CC2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.47 | P42:345:OPPD:S3740-S3455&CC2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.47 | P43:015-345:OPPD:S3740-S3455&CC2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.57 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.64 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.64 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.79 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 142.03 | P23:345:XEL:8P2 KING | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 142.83 | Potential P4 Event - POI 645740_2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 142.96 | P23:345:MEC:CBEC 908 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.93 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.94 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.96 | 514715 WOODRNG7 345 762321 GEN-2017-164 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.96 | 514787 DEWEY 4 138 766160 GEN-2021-098 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.97 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.97 | 515802 GRACMNT4 138 774981 GEN-2023-150 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.98 | 514801 MINCO 7 345 761250 GEN-2017-233 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.98 | 515543 RENFROW7 345 760809 GEN-2017-203 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.98 | 523267 PRINGLE 6 230 774441 GEN-2023-123 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.98 | 523309 MOORE_CNTY 6 230 772181 GEN-2023-010 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.99 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.99 | 655840 CHRRYCRK-MK7 115 655876 DPLWCTAP-MK7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.99 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.2 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.21 | 509829 FULTONW4 138 509830 KENSH-E-TP4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.21 | 511560 GRADY 4 138 511567 CHOCTAW4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.22 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.25 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.29 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.3 | P12:138:OKGE:BKRBKR176:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.35 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.36 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.42 | 640278 SHELDON7 115 640021 HALLAM3G 13.8 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.47 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.47 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.48 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.48 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.48 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.48 | P13:NI901T/902T/903T GSU | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.54 | 762779 G18-043 TAP 345 762780 GEN-2018-043 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.54 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.54 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.58 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.58 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.6 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.6 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.67 | P13:SH902T GSU | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.69 | P11:024:DPC:ALMA2:6 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.69 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.69 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.75 | P11:18:SPC: BD #6:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.8 | P11:18:SPC:GPPS#1 GT+SSL - FUT:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.8 | P12:138:OKGE:BKRBKR130:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.82 | P11:18:SPC:GPPS#1GT-FUT:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.92 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.11 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.19 | GEN-2021-043_POI_650290_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.28 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.28 | P23:345:XEL:8N17 SHC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.28 | P23:345:XEL:8N22 SHC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.29 | 640427 STEELEC9 4.16 640426 STEELEC7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.29 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.29 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.31 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.32 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.33 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.36 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.36 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.41 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.58 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.63 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.73 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.9 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.97 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.97 | Potential P4 Event - POI 659333_5 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.07 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.1 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.1 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.1 | Potential P4 Event - POI 640590_10 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.1 | Potential P4 Event - POI 640590_11 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.11 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.19 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.42 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.46 | Potential P4 Event - POI 645740_12 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 145.01 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 145.11 | GEN-2023-224_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 145.11 | Potential P4 Event - POI 640590_9 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 147.65 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31146 | 141.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31146 | 141.53 | P12:345:OKGE:BKRBKR357_1:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31147 | 141.58 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 141.36 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.35 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.45 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31162 | 141.32 | P12:115:HAST:::LINE | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3123 | 142.27 | P21:161:OPPD:HUMBOLT-S1398:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3123 | 142.28 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31272 | 141.6 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31272 | 141.62 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31548 | 142.77 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31548 | 142.89 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31618 | 142.74 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31618 | 143.64 | P12:115:WERE:KNOB-MKEC-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31618 | 143.66 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.32882 | 154.7 | P12:115:WERE:KNOB-NPPD-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34901 | 158.38 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34901 | 158.38 | P13:115-161:NPPD:HUMBOLT5:T2::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34901 | 159.72 | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34901 | 160.16 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34901 | 160.18 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.37284 | 175.63 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.55392 | 249.59 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.38615 | 133.36 | GEN-2023-225_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40199 | 132.69 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40238 | 132.68 | Potential P4 Event - POI 640226_4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4025 | 132.33 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40251 | 131.86 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40253 | 133.54 | P23:345:MEC:CBEC 905 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40254 | 131.98 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40254 | 132.35 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40254 | 132.76 | Potential P4 Event - POI 640226_3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40254 | 133.4 | Potential P4 Event - POI 640226_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 131.81 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 131.82 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 131.82 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 131.83 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 131.89 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 131.92 | 541198 PECULR 7 345 541200 PHILL 7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 132.15 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 132.16 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 132.3 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 133.29 | Potential P4 Event - POI 645740_2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 130.75 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.37 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.48 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.48 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.5 | 508563 PIRKEY 7 345 769761 GEN-2022-139 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.51 | 514715 WOODRNG7 345 762321 GEN-2017-164 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.51 | 514787 DEWEY 4 138 766160 GEN-2021-098 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.52 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.52 | 507751 RDPOINT4 138 776581 GEN-2023-230 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.52 | 515543 RENFROW7 345 760809 GEN-2017-203 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.52 | 515802 GRACMNT4 138 774981 GEN-2023-150 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.53 | 514801 MINCO 7 345 761250 GEN-2017-233 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.53 | 523267 PRINGLE 6 230 774441 GEN-2023-123 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.53 | 523309 MOORE_CNTY 6 230 772181 GEN-2023-010 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.53 | 655836 OAKDALE -MK7 115 655853 BEARCREK-MK7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.73 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.73 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.74 | 511560 GRADY 4 138 511567 CHOCTAW4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.75 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.75 | 509829 FULTONW4 138 509830 KENSH-E-TP4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.76 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.76 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.76 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.76 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.77 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.79 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.81 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.82 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.83 | P12:138:OKGE:BKRBKR176:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.83 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.88 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.88 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.88 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.89 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.89 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.94 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.94 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.94 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.96 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.96 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.96 | P23:500:EES:PERVIL:R9872 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.96 | P23:500:EMI:ABF_PRYVL-A | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.97 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.99 | P41:345:OPPD:S3740-55&CC2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.99 | P42:345:OPPD:S3740-S3455&CC2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.99 | P43:015-345:OPPD:S3740-S3455&CC2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.01 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.01 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.01 | P13:NI901T/902T/903T GSU | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.06 | 762779 G18-043 TAP 345 762780 GEN-2018-043 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.06 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.06 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.09 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.1 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.1 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.12 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.12 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.19 | P13:SH902T GSU | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.2 | P11:024:DPC:ALMA2:6 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.2 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.21 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.27 | P11:18:SPC: BD #6:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.31 | P11:18:SPC:GPPS#1 GT+SSL - FUT:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.31 | P12:138:OKGE:BKRBKR130:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.33 | P11:18:SPC:GPPS#1GT-FUT:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.42 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.53 | P23:345:XEL:8P2 KING | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.61 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.68 | GEN-2021-043_POI_650290_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.77 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.77 | P23:345:XEL:8N17 SHC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.77 | P23:345:XEL:8N22 SHC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.78 | 640427 STEELEC9 4.16 640426 STEELEC7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.78 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.78 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.8 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.81 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.82 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.85 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.85 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.9 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.06 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.1 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.2 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.36 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.42 | P23:345:MEC:CBEC 908 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.43 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.43 | Potential P4 Event - POI 659333_5 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.46 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.52 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.55 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.55 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.55 | Potential P4 Event - POI 640590_10 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.55 | Potential P4 Event - POI 640590_11 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.56 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.64 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.86 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.91 | Potential P4 Event - POI 645740_12 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 135.38 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 135.47 | GEN-2023-224_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 135.48 | Potential P4 Event - POI 640590_9 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 137.9 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40257 | 132.05 | P12:345:OKGE:BKRBKR357_1:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40258 | 131.73 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40259 | 132.1 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4026 | 131.89 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.87 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.97 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40279 | 131.85 | P12:115:HAST:::LINE | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40366 | 132.76 | P21:161:OPPD:HUMBOLT-S1398:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40366 | 132.77 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40421 | 132.12 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40421 | 132.14 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40778 | 133.24 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40778 | 133.35 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40868 | 133.21 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40868 | 134.07 | P12:115:WERE:KNOB-MKEC-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40868 | 134.09 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.42502 | 144.66 | P12:115:WERE:KNOB-NPPD-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45112 | 148.18 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45112 | 149.89 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45112 | 149.9 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.48191 | 164.69 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60871 | 195.57 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60871 | 198.73 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60871 | 198.98 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 771999 G23-222-POI 345 776422 G23-222XFMR1 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 771999 G23-222-POI 345 776425 G23-222XFMR2 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 771999 G23-222-POI 345 776442 G23-223XFMR1 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 776422 G23-222XFMR1 345 776424 G23-222GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 776425 G23-222XFMR2 345 776427 G23-222GEN2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 776442 G23-223XFMR1 345 776444 G23-223GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | GEN-2023-223_POI_771999_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.29874 | 139.43 | GEN-2023-225_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.311 | 138.72 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31131 | 138.71 | Potential P4 Event - POI 640226_4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3114 | 138.33 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31141 | 137.84 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31142 | 139.62 | P23:345:MEC:CBEC 905 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31143 | 137.78 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31143 | 137.97 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31143 | 138.36 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31143 | 138.79 | Potential P4 Event - POI 640226_3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31143 | 139.46 | Potential P4 Event - POI 640226_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.49 | 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.49 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.69 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.7 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.71 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.72 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.73 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.73 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.73 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.78 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.79 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.79 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.8 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.8 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.85 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.85 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.86 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.87 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.9 | 541198 PECULR 7 345 541200 PHILL 7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.92 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.92 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.94 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.94 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.94 | P23:500:EES:PERVIL:R9872 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.94 | P23:500:EMI:ABF_PRYVL-A | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.95 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.96 | P41:345:OPPD:S3740-55&CC2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.96 | P42:345:OPPD:S3740-S3455&CC2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.96 | P45:345:OPPD:S3740-S3455&CC2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 138.07 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 138.15 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 138.15 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 138.3 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 138.55 | P23:345:XEL:8P2 KING | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 139.36 | Potential P4 Event - POI 645740_2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 139.49 | P23:345:MEC:CBEC 908 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.43 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.43 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.46 | 514715 WOODRNG7 345 762321 GEN-2017-164 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.46 | 514787 DEWEY 4 138 766160 GEN-2021-098 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.47 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.47 | 515802 GRACMNT4 138 774981 GEN-2023-150 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.48 | 514801 MINCO 7 345 761250 GEN-2017-233 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.48 | 515543 RENFROW7 345 760809 GEN-2017-203 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.48 | 523267 PRINGLE 6 230 774441 GEN-2023-123 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.48 | 523309 MOORE_CNTY 6 230 772181 GEN-2023-010 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.49 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.49 | 655840 CHRRYCRK-MK7 115 655876 DPLWCTAP-MK7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.49 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.7 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.71 | 511560 GRADY 4 138 511567 CHOCTAW4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.72 | 509829 FULTONW4 138 509830 KENSH-E-TP4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.73 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.76 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.79 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.8 | P12:138:OKGE:BKRBKR176:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.86 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.86 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.92 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.98 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.98 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.99 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.99 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.99 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.99 | P13:NI901T/902T/903T GSU | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.05 | 762779 G18-043 TAP 345 762780 GEN-2018-043 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.05 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.05 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.09 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.09 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.11 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.11 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.18 | P13:SH902T GSU | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.2 | P11:024:DPC:ALMA2:6 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.2 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.21 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.27 | P11:18:SPC: BD #6:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.31 | P11:18:SPC:GPPS#1 GT+SSL - FUT:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.31 | P12:138:OKGE:BKRBKR130:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.34 | P11:18:SPC:GPPS#1GT-FUT:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.43 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.64 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.71 | GEN-2021-043_POI_650290_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.8 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.81 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.81 | P23:345:XEL:8N17 SHC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.81 | P23:345:XEL:8N22 SHC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.82 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.83 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.84 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.86 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.89 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.89 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.94 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.11 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.16 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.26 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.43 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.5 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.51 | Potential P4 Event - POI 659333_5 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.54 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.61 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.64 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.64 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.64 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.64 | Potential P4 Event - POI 640590_12 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.64 | Potential P4 Event - POI 640590_13 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.72 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.96 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 140.01 | Potential P4 Event - POI 645740_12 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 141.49 | 640112 CLATONA9 34.5 3WXFMR CLATONIA T1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 141.58 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 141.68 | GEN-2023-224_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 141.68 | Potential P4 Event - POI 640590_9 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 144.27 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31146 | 137.7 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31146 | 138.04 | P12:345:OKGE:BKRBKR357_1:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31147 | 138.09 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 137.86 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.85 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.96 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31162 | 137.82 | P12:115:HAST:::LINE | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3123 | 138.79 | P21:161:OPPD:HUMBOLT-S1398:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3123 | 138.81 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31272 | 138.11 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31272 | 138.13 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31548 | 139.3 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31548 | 139.42 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31618 | 139.27 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31618 | 140.19 | P12:115:WERE:KNOB-MKEC-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31618 | 140.21 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.32882 | 151.46 | P12:115:WERE:KNOB-NPPD-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34901 | 155.21 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34901 | 155.21 | P13:115-161:NPPD:HUMBOLT5:T2::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34901 | 156.58 | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34901 | 157.03 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34901 | 157.04 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.37284 | 172.8 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.55392 | 248.32 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.11557 | 106.74 | P12:115:WERE:KNOB-NPPD-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.11691 | 110.08 | 640208 HARBINE7 115 640426 STEELEC7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.13033 | 103.65 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.13033 | 104.82 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.13033 | 104.87 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.14928 | 117.05 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | 121 | 121 | 0.17946 | 101.49 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 640278 SHELDON7 115 650246 SW7&BENNET7 115 1 | 240 | 240 | 0.14854 | 103.19 | Potential P4 Event - POI 640590_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 771999 G23-222-POI 345 776422 G23-222XFMR1 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 771999 G23-222-POI 345 776425 G23-222XFMR2 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 771999 G23-222-POI 345 776442 G23-223XFMR1 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 776422 G23-222XFMR1 345 776424 G23-222GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 776425 G23-222XFMR2 345 776427 G23-222GEN2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 776442 G23-223XFMR1 345 776444 G23-223GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | GEN-2023-223_POI_771999_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 547469 RIV4525 161 547498 STL439 5 161 1 | 461 | 461 | 0.07367 | 100.35 | 547467 ORO110 5 161 547469 RIV4525 161 1 | Cumulative Impact | RIV4525 to STL439 Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | 193 | 193 | 0.27226 | 139.25 | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 193 | 193 | 0.22818 | 101.08 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 193 | 193 | 0.27341 | 139.83 | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.16844 | 147.89 | P13:115-230:SUNC:CONCORDIA_XFR:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17129 | 141.92 | 539805 ELMCREEK7 345 3WXFMR ELMCREEK T1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17199 | 141.52 | 532765 HOYT 7 345 3WXFMR HOYT1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 141.55 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17218 | 141.03 | P42:345:OKGE:SB_RARD7381:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17218 | 141.51 | P13:115:WERE:EMAN-TX-3-230-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17218 | 143.19 | Potential P4 Event - POI 515576_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.6 | P13:69-161:XEL:AUTO-SINGLE:WBYRON8:BYRON5:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.64 | 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.68 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.68 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.77 | P12:115:XEL:AUTO-SINGLE:NSSTAP7:NSSTL7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.77 | P21:115:XEL:AUTO-SINGLE:NSSTAP7:NSSTL7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.82 | P12:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.82 | P21:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.84 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.86 | P21:115:XEL:AUTO-SINGLE:REDROCK7:NSSJCT7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.88 | P12:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.89 | 506944 CHAMSPR5 161 776241 GEN-2023-213 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.89 | 512635 KERR GR5 161 773081 GEN-2023-055 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.89 | 528013 PHANTOM 3 115 775661 GEN-2023-184 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.92 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.93 | 508298 LYDIA 7 345 764075 GEN-2020-054 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.93 | P12:345:XEL:ASK-ECL SPS | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.96 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.97 | 505522 VAN BUR5 161 773101 GEN-2023-056 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 139.99 | 526936 YOAKUM 7 345 766120 GEN-2021-090 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.01 | 515235 PECANCK7 345 762823 GEN-2018-048 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.03 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.04 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.05 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.12 | 640230 HOSK.T89 34.5 640227 HOSKINS4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.15 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.15 | 509782 R.S.S.-7 345 588040 G16133G16146 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.22 | P12:138:AEPW:ARSHILL4:STLGENS4::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.24 | 512749 PAWNSW4 138 773121 GEN-2023-057 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.29 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.31 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.37 | P13:161-22:AEPW:FLINTCR5:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.41 | 514922 CLASSEN4 138 775341 GEN-2023-168 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.46 | 640112 CLATONA9 34.5 3WXFMR CLATONIA T1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.5 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.53 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.53 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.54 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.56 | 560053 G15052_T 345 562900 G15052_1 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.56 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.57 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.58 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.6 | P11:345:GRDA:GRDA17-1:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.61 | P13:345:GRDA:GRDA2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.61 | P41:345:GRDA:GRDA CB320:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.63 | P12:161:GRDA:SALINA 5-SALNCRK5:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.63 | P13:138-24:AEPW:TURK 4:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.66 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.74 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.75 | P23:500:EES-EAI:WH_BLF:B7942 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.79 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 140.82 | 515156 WASHPRK4 138 775321 GEN-2023-167 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.03 | 776061 GEN-2023-204 345 776067 G23-204GEN2 23.5 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.13 | 525481 PLANT_X 6 230 774821 GEN-2023-142 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.13 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.18 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.2 | 532793 NEOSHO 7 345 772981 GEN-2023-050 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.22 | 532766 JEC N 7 345 766240 GEN-2021-107 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.23 | 515852 DGRASSE7 345 773981 GEN-2023-100 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.32 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.4 | 527000 GAINES_PLNT7 345 527020 SIDEWINDER 7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.65 | P11:HV:EES::1RVR_BND_G1!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.65 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.65 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.65 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.69 | 525832 TUCO_INT 7 345 525850 ELK_CT1 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.69 | 525832 TUCO_INT 7 345 769921 GEN-2022-147 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.7 | 515800 GRACMNT7 345 775261 GEN-2023-164 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.71 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.8 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.89 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.89 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.89 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.9 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 141.9 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 142 | 515852 DGRASSE7 345 776821 GEN-2023-102 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 142.01 | GEN-2023-102_POI_515852_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 142.05 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 142.05 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 142.15 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 142.15 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 142.63 | Potential P4 Event - POI 515576_20 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 142.65 | 776060 G23-204-TAP 345 776061 GEN-2023-204 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 142.65 | GEN-2023-204_POI_776060_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 142.85 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 143.78 | 640218 HEBRN N7 115 640012 HEBRON G 13.8 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 144 | Potential P4 Event - POI 525832_3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 145.41 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 146.54 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 159.59 | 640208 HARBINE7 115 772201 GEN-2023-011 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 159.59 | 772201 GEN-2023-011 115 772202 G23-011XFMR1 34.5 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17219 | 159.59 | GEN-2023-011_POI_640208_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1722 | 139.64 | 659425 SD.LS-KS-MB3 345 763666 G21-037-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1722 | 139.66 | 338120 5S.LEAD HILL 161 505461 BULL SH W5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1722 | 139.96 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:HCKRYCK3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1722 | 140.02 | P23:345:ITCM:HAZLTON3 9985:IA-NE | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1722 | 140.04 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1722 | 140.09 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1722 | 146.61 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17221 | 139.89 | P12:345:XEL:AUTO-SINGLE:WILMART3:SHEASLK3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17221 | 140.43 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17221 | 140.67 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17224 | 141.48 | P42:500:OKGE:SB_FTTH8581:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17224 | 141.48 | P42:500:OKGE:SB_FTTH8585:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17224 | 141.5 | P12:500:OKGE-EESAR:OKGE-EESEAI:BKRBKR317::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17224 | 141.5 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17226 | 140.25 | 300041 7FRANKS 345 300051 7FRANKSRCTP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17226 | 140.25 | 300042 7HUBEN 345 300051 7FRANKSRCTP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17228 | 140.27 | 635580 ARBOR HILL 3 345 635590 FALLOW AVE 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17228 | 140.67 | 635580 ARBOR HILL 3 345 635622 RCCN TRL 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17234 | 141.33 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17234 | 141.33 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17234 | 141.37 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1724 | 140.04 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1724 | 140.26 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1724 | 140.26 | P23:345:MEC:BONDURANT:906::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1724 | 140.27 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1724 | 140.27 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1724 | 140.69 | P23:345:MEC:MONTEZUMA:902::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17264 | 141.45 | 300039 7FAIRPT 345 640139 COOPER 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1728 | 141.65 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1728 | 141.66 | 541197 MULLNCR7 345 771140 G22-208-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1728 | 141.67 | 541197 MULLNCR7 345 541510 HOLT 7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17281 | 143.51 | Potential P4 Event - POI 532772_9 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17306 | 147.03 | 532913 KELLY 5 161 3WXFMR KELL TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17307 | 142.71 | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17328 | 143.11 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17328 | 143.11 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17506 | 149.4 | P12:161:WERE:TECH-KELL-OPPD-161:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17506 | 149.4 | P12:161:WERE-OPPD:S1399-KELLY:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17512 | 144.65 | Potential P4 Event - POI 640271_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17682 | 148.72 | P21:161:OPPD:S1399-KELLY:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17768 | 150.29 | Potential P4 Event - POI 640590_7 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17768 | 150.29 | Potential P4 Event - POI 640590_8 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17924 | 145.49 | Potential P4 Event - POI 640271_1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.187 | 164 | Potential P4 Event - POI 640590_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.19987 | 156.79 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.19987 | 158.58 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.2343 | 175.6 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.2343 | 177.52 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.2343 | 177.77 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.26662 | 198.16 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640361 STEINER7 115 1 | 121 | 121 | 0.17946 | 103.33 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.29874 | 142.9 | GEN-2023-225_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.311 | 142.19 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31131 | 142.19 | Potential P4 Event - POI 640226_4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3114 | 141.82 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31141 | 141.33 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31142 | 143.08 | P23:345:MEC:CBEC 905 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31143 | 141.27 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31143 | 141.46 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31143 | 141.84 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31143 | 142.27 | Potential P4 Event - POI 640226_3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31143 | 142.94 | Potential P4 Event - POI 640226_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 140.99 | 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 140.99 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.19 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.19 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.21 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.22 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.22 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.23 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.23 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.28 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.28 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.29 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.3 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.3 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.35 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.35 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.36 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.36 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.39 | 541198 PECULR 7 345 541200 PHILL 7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.42 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.42 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.43 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.43 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.43 | P23:500:EES:PERVIL:R9872 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.43 | P23:500:EMI:ABF_PRYVL-A | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.44 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.47 | P41:345:OPPD:S3740-55&CC2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.47 | P42:345:OPPD:S3740-S3455&CC2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.47 | P43:015-345:OPPD:S3740-S3455&CC2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.57 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.64 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.64 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 141.79 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 142.03 | P23:345:XEL:8P2 KING | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 142.83 | Potential P4 Event - POI 645740_2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31144 | 142.96 | P23:345:MEC:CBEC 908 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.93 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.94 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.96 | 514715 WOODRNG7 345 762321 GEN-2017-164 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.96 | 514787 DEWEY 4 138 766160 GEN-2021-098 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.97 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.97 | 515802 GRACMNT4 138 774981 GEN-2023-150 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.98 | 514801 MINCO 7 345 761250 GEN-2017-233 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.98 | 515543 RENFROW7 345 760809 GEN-2017-203 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.98 | 523267 PRINGLE 6 230 774441 GEN-2023-123 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.98 | 523309 MOORE_CNTY 6 230 772181 GEN-2023-010 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.99 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.99 | 655840 CHRRYCRK-MK7 115 655876 DPLWCTAP-MK7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 140.99 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.2 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.21 | 509829 FULTONW4 138 509830 KENSH-E-TP4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.21 | 511560 GRADY 4 138 511567 CHOCTAW4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.22 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.25 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.29 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.3 | P12:138:OKGE:BKRBKR176:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.35 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.36 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.42 | 640278 SHELDON7 115 640021 HALLAM3G 13.8 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.47 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.47 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.48 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.48 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.48 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.48 | P13:NI901T/902T/903T GSU | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.54 | 762779 G18-043 TAP 345 762780 GEN-2018-043 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.54 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.54 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.58 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.58 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.6 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.6 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.67 | P13:SH902T GSU | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.69 | P11:024:DPC:ALMA2:6 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.69 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.69 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.75 | P11:18:SPC: BD #6:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.8 | P11:18:SPC:GPPS#1 GT+SSL - FUT:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.8 | P12:138:OKGE:BKRBKR130:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.82 | P11:18:SPC:GPPS#1GT-FUT:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 141.92 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.11 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.19 | GEN-2021-043_POI_650290_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.28 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.28 | P23:345:XEL:8N17 SHC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.28 | P23:345:XEL:8N22 SHC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.29 | 640427 STEELEC9 4.16 640426 STEELEC7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.29 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.29 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.31 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.32 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.33 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.36 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.36 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.41 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.58 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.63 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.73 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.9 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.97 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 142.97 | Potential P4 Event - POI 659333_5 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.07 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.1 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.1 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.1 | Potential P4 Event - POI 640590_10 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.1 | Potential P4 Event - POI 640590_11 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.11 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.19 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.42 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 143.46 | Potential P4 Event - POI 645740_12 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 145.01 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 145.11 | GEN-2023-224_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 145.11 | Potential P4 Event - POI 640590_9 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31145 | 147.65 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31146 | 141.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31146 | 141.53 | P12:345:OKGE:BKRBKR357_1:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31147 | 141.58 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31148 | 141.36 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.35 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31149 | 141.45 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31162 | 141.32 | P12:115:HAST:::LINE | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3123 | 142.27 | P21:161:OPPD:HUMBOLT-S1398:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.3123 | 142.28 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31272 | 141.6 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31272 | 141.62 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31548 | 142.77 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31548 | 142.89 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31618 | 142.74 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31618 | 143.64 | P12:115:WERE:KNOB-MKEC-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31618 | 143.66 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.32882 | 154.7 | P12:115:WERE:KNOB-NPPD-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34901 | 158.38 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34901 | 158.38 | P13:115-161:NPPD:HUMBOLT5:T2::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34901 | 159.72 | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34901 | 160.16 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34901 | 160.18 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.37284 | 175.63 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.55392 | 249.59 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.38615 | 133.36 | GEN-2023-225_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40199 | 132.69 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40238 | 132.68 | Potential P4 Event - POI 640226_4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4025 | 132.33 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40251 | 131.86 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40253 | 133.54 | P23:345:MEC:CBEC 905 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40254 | 131.98 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40254 | 132.35 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40254 | 132.76 | Potential P4 Event - POI 640226_3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40254 | 133.4 | Potential P4 Event - POI 640226_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 131.81 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 131.82 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 131.82 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 131.83 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 131.89 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 131.92 | 541198 PECULR 7 345 541200 PHILL 7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 132.15 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 132.16 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 132.3 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40255 | 133.29 | Potential P4 Event - POI 645740_2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 130.75 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.37 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.48 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.48 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.5 | 508563 PIRKEY 7 345 769761 GEN-2022-139 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.51 | 514715 WOODRNG7 345 762321 GEN-2017-164 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.51 | 514787 DEWEY 4 138 766160 GEN-2021-098 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.52 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.52 | 507751 RDPOINT4 138 776581 GEN-2023-230 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.52 | 515543 RENFROW7 345 760809 GEN-2017-203 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.52 | 515802 GRACMNT4 138 774981 GEN-2023-150 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.53 | 514801 MINCO 7 345 761250 GEN-2017-233 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.53 | 523267 PRINGLE 6 230 774441 GEN-2023-123 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.53 | 523309 MOORE_CNTY 6 230 772181 GEN-2023-010 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.53 | 655836 OAKDALE -MK7 115 655853 BEARCREK-MK7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.73 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.73 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.74 | 511560 GRADY 4 138 511567 CHOCTAW4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.75 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.75 | 509829 FULTONW4 138 509830 KENSH-E-TP4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.76 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.76 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.76 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.76 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.77 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.79 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.81 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.82 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.83 | P12:138:OKGE:BKRBKR176:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.83 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.88 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.88 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.88 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.89 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.89 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.94 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.94 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.94 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.96 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.96 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.96 | P23:500:EES:PERVIL:R9872 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.96 | P23:500:EMI:ABF_PRYVL-A | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.97 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.99 | P41:345:OPPD:S3740-55&CC2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.99 | P42:345:OPPD:S3740-S3455&CC2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 131.99 | P43:015-345:OPPD:S3740-S3455&CC2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.01 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.01 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.01 | P13:NI901T/902T/903T GSU | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.06 | 762779 G18-043 TAP 345 762780 GEN-2018-043 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.06 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.06 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.09 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.1 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.1 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.12 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.12 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.19 | P13:SH902T GSU | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.2 | P11:024:DPC:ALMA2:6 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.2 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.21 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.27 | P11:18:SPC: BD #6:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.31 | P11:18:SPC:GPPS#1 GT+SSL - FUT:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.31 | P12:138:OKGE:BKRBKR130:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.33 | P11:18:SPC:GPPS#1GT-FUT:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.42 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.53 | P23:345:XEL:8P2 KING | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.61 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.68 | GEN-2021-043_POI_650290_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.77 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.77 | P23:345:XEL:8N17 SHC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.77 | P23:345:XEL:8N22 SHC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.78 | 640427 STEELEC9 4.16 640426 STEELEC7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.78 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.78 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.8 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.81 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.82 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.85 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.85 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 132.9 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.06 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.1 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.2 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.36 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.42 | P23:345:MEC:CBEC 908 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.43 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.43 | Potential P4 Event - POI 659333_5 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.46 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.52 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.55 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.55 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.55 | Potential P4 Event - POI 640590_10 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.55 | Potential P4 Event - POI 640590_11 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.56 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.64 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.86 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 133.91 | Potential P4 Event - POI 645740_12 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 135.38 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 135.47 | GEN-2023-224_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 135.48 | Potential P4 Event - POI 640590_9 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40256 | 137.9 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40257 | 132.05 | P12:345:OKGE:BKRBKR357_1:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40258 | 131.73 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40259 | 132.1 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4026 | 131.89 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.87 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40262 | 131.97 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40279 | 131.85 | P12:115:HAST:::LINE | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40366 | 132.76 | P21:161:OPPD:HUMBOLT-S1398:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40366 | 132.77 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40421 | 132.12 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40421 | 132.14 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40778 | 133.24 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40778 | 133.35 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40868 | 133.21 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40868 | 134.07 | P12:115:WERE:KNOB-MKEC-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40868 | 134.09 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.42502 | 144.66 | P12:115:WERE:KNOB-NPPD-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45112 | 148.18 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45112 | 149.89 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45112 | 149.9 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.48191 | 164.69 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60871 | 195.57 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60871 | 198.73 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60871 | 198.98 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 771999 G23-222-POI 345 776422 G23-222XFMR1 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 771999 G23-222-POI 345 776425 G23-222XFMR2 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 776422 G23-222XFMR1 345 776424 G23-222GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.6 | 776425 G23-222XFMR2 345 776427 G23-222GEN2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.29874 | 139.43 | GEN-2023-225_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.311 | 138.72 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31131 | 138.71 | Potential P4 Event - POI 640226_4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3114 | 138.33 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31141 | 137.84 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31142 | 139.62 | P23:345:MEC:CBEC 905 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31143 | 137.78 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31143 | 137.97 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31143 | 138.36 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31143 | 138.79 | Potential P4 Event - POI 640226_3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31143 | 139.46 | Potential P4 Event - POI 640226_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.49 | 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.49 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.69 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.7 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.71 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.72 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.73 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.73 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.73 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.78 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.79 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.79 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.8 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.8 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.85 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.85 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.86 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.87 | P12:EHV:EES::8DRIVER%:8SHELBYTN!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.9 | 541198 PECULR 7 345 541200 PHILL 7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.92 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.92 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.94 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.94 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.94 | P23:500:EES:PERVIL:R9872 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.94 | P23:500:EMI:ABF_PRYVL-A | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.95 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.96 | P41:345:OPPD:S3740-55&CC2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.96 | P42:345:OPPD:S3740-S3455&CC2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 137.96 | P45:345:OPPD:S3740-S3455&CC2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 138.07 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 138.15 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 138.15 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 138.3 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 138.55 | P23:345:XEL:8P2 KING | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 139.36 | Potential P4 Event - POI 645740_2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31144 | 139.49 | P23:345:MEC:CBEC 908 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.43 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.43 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.46 | 514715 WOODRNG7 345 762321 GEN-2017-164 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.46 | 514787 DEWEY 4 138 766160 GEN-2021-098 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.47 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.47 | 515802 GRACMNT4 138 774981 GEN-2023-150 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.48 | 514801 MINCO 7 345 761250 GEN-2017-233 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.48 | 515543 RENFROW7 345 760809 GEN-2017-203 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.48 | 523267 PRINGLE 6 230 774441 GEN-2023-123 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.48 | 523309 MOORE_CNTY 6 230 772181 GEN-2023-010 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.49 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.49 | 655840 CHRRYCRK-MK7 115 655876 DPLWCTAP-MK7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.49 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.7 | 532874 UNIONRG6 230 3WXFMR UNIO TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.71 | 511560 GRADY 4 138 511567 CHOCTAW4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.72 | 509829 FULTONW4 138 509830 KENSH-E-TP4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.73 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.76 | 509811 T.S.E.-4 138 509830 KENSH-E-TP4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.79 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.8 | P12:138:OKGE:BKRBKR176:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.86 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.86 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.92 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.98 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.98 | 652538 WHITE 7 115 773621 GEN-2023-082 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.99 | 539711 GRNLEAF1 34.5 3WXFMR GRNLEAF3 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.99 | 635425 PALO ALTO 3 345 635432 J529J590 SUB 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.99 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 137.99 | P13:NI901T/902T/903T GSU | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.05 | 762779 G18-043 TAP 345 762780 GEN-2018-043 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.05 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.05 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.09 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.09 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.11 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.11 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.18 | P13:SH902T GSU | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.2 | P11:024:DPC:ALMA2:6 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.2 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.21 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.27 | P11:18:SPC: BD #6:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.31 | P11:18:SPC:GPPS#1 GT+SSL - FUT:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.31 | P12:138:OKGE:BKRBKR130:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.34 | P11:18:SPC:GPPS#1GT-FUT:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.43 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.64 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.71 | GEN-2021-043_POI_650290_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.8 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.81 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.81 | P23:345:XEL:8N17 SHC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.81 | P23:345:XEL:8N22 SHC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.82 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.83 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.84 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.86 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.89 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.89 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 138.94 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.11 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.16 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.26 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.43 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.5 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.51 | Potential P4 Event - POI 659333_5 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.54 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.61 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.64 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.64 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.64 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.64 | Potential P4 Event - POI 640590_12 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.64 | Potential P4 Event - POI 640590_13 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.72 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 139.96 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 140.01 | Potential P4 Event - POI 645740_12 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 141.49 | 640112 CLATONA9 34.5 3WXFMR CLATONIA T1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 141.58 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 141.68 | GEN-2023-224_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 141.68 | Potential P4 Event - POI 640590_9 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31145 | 144.27 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31146 | 137.7 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31146 | 138.04 | P12:345:OKGE:BKRBKR357_1:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31147 | 138.09 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31148 | 137.86 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.85 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31149 | 137.96 | 635018 WESTBORO 3 345 635570 ORIENT 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31162 | 137.82 | P12:115:HAST:::LINE | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3123 | 138.79 | P21:161:OPPD:HUMBOLT-S1398:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.3123 | 138.81 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31272 | 138.11 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31272 | 138.13 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31548 | 139.3 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31548 | 139.42 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31618 | 139.27 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31618 | 140.19 | P12:115:WERE:KNOB-MKEC-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31618 | 140.21 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.32882 | 151.46 | P12:115:WERE:KNOB-NPPD-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34901 | 155.21 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34901 | 155.21 | P13:115-161:NPPD:HUMBOLT5:T2::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34901 | 156.58 | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34901 | 157.03 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34901 | 157.04 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.37284 | 172.8 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.55392 | 248.32 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.11557 | 106.74 | P12:115:WERE:KNOB-NPPD-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.11691 | 110.08 | 640208 HARBINE7 115 640426 STEELEC7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.13033 | 103.65 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.13033 | 104.82 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.13033 | 104.87 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.14928 | 117.05 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | 121 | 121 | 0.17946 | 101.49 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 640278 SHELDON7 115 650246 SW7&BENNET7 115 1 | 240 | 240 | 0.14854 | 103.19 | Potential P4 Event - POI 640590_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 771999 G23-222-POI 345 776422 G23-222XFMR1 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 771999 G23-222-POI 345 776425 G23-222XFMR2 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 776422 G23-222XFMR1 345 776424 G23-222GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.1 | 776425 G23-222XFMR2 345 776427 G23-222GEN2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-224 | FROM->TO | 547469 RIV4525 161 547498 STL439 5 161 1 | 461 | 461 | 0.07289 | 100.35 | 547467 ORO110 5 161 547469 RIV4525 161 1 | Cumulative Impact | RIV4525 to STL439 Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-224 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.05936 | 164 | Potential P4 Event - POI 640590_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-224 | FROM->TO | 640278 SHELDON7 115 650246 SW7&BENNET7 115 1 | 240 | 240 | 0.19132 | 103.19 | Potential P4 Event - POI 640590_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-225 | FROM->TO | 547469 RIV4525 161 547498 STL439 5 161 1 | 461 | 461 | 0.07289 | 100.35 | 547467 ORO110 5 161 547469 RIV4525 161 1 | Cumulative Impact | RIV4525 to STL439 Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-225 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.05936 | 164 | Potential P4 Event - POI 640590_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27SP | GEN-2023-225 | FROM->TO | 640278 SHELDON7 115 650246 SW7&BENNET7 115 1 | 240 | 240 | 0.19132 | 103.19 | Potential P4 Event - POI 640590_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.5901 | 101.17 | 509050 KEATCHI4 138 509052 STONWAL4 138 1 | Cumulative Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.5901 | 102.22 | 507793 LEASIDE 4 138 509052 STONWAL4 138 1 | Cumulative Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.60098 | 103.99 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.60098 | 103.99 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.60098 | 103.99 | Potential P4 Event - POI 508359_5 | Cumulative Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.05812 | 107.44 | 533021 NEOSHO 4 138 533023 N345 3 4 138 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.05812 | 107.86 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.05812 | 104.96 | 533021 NEOSHO 4 138 533023 N345 3 4 138 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.05812 | 105.16 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 547467 ORO110 5 161 547469 RIV4525 161 1 | 404 | 420 | 0.06948 | 106.9 | 547469 RIV4525 161 547498 STL439 5 161 1 | Cumulative Impact | ORO11505 to RIV4525 Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-062 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.07079 | 107.44 | 533021 NEOSHO 4 138 533023 N345 3 4 138 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-062 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.07079 | 107.86 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-062 | FROM->TO | 532793 NEOSHO 7 345 997417 N345 TX-1 138 1 | 400 | 440 | 0.05572 | 112.27 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-062 | FROM->TO | 532793 NEOSHO 7 345 997417 N345 TX-1 138 1 | 400 | 440 | 0.05572 | 112.49 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-062 | FROM->TO | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.07079 | 104.96 | 533021 NEOSHO 4 138 533023 N345 3 4 138 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-062 | FROM->TO | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.07079 | 105.16 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-062 | FROM->TO | 533023 N345 3 4 138 997417 N345 TX-1 138 1 | 400 | 440 | 0.05572 | 108.44 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-062 | FROM->TO | 533023 N345 3 4 138 997417 N345 TX-1 138 1 | 400 | 440 | 0.05572 | 108.51 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-062 | FROM->TO | 547467 ORO110 5 161 547469 RIV4525 161 1 | 404 | 420 | 0.07044 | 106.9 | 547469 RIV4525 161 547498 STL439 5 161 1 | Cumulative Impact | ORO11505 to RIV4525 Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-077 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.07424 | 107.44 | 533021 NEOSHO 4 138 533023 N345 3 4 138 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-077 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.07424 | 107.86 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-077 | FROM->TO | 532793 NEOSHO 7 345 997417 N345 TX-1 138 1 | 400 | 440 | 0.05849 | 112.27 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-077 | FROM->TO | 532793 NEOSHO 7 345 997417 N345 TX-1 138 1 | 400 | 440 | 0.05849 | 112.49 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-077 | FROM->TO | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.07424 | 104.96 | 533021 NEOSHO 4 138 533023 N345 3 4 138 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-077 | FROM->TO | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.07424 | 105.16 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-077 | FROM->TO | 533023 N345 3 4 138 997417 N345 TX-1 138 1 | 400 | 440 | 0.05849 | 108.44 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-077 | FROM->TO | 533023 N345 3 4 138 997417 N345 TX-1 138 1 | 400 | 440 | 0.05849 | 108.51 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-077 | FROM->TO | 547467 ORO110 5 161 547469 RIV4525 161 1 | 404 | 420 | 0.07278 | 106.9 | 547469 RIV4525 161 547498 STL439 5 161 1 | Cumulative Impact | ORO11505 to RIV4525 Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-077 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 1 | 123.27 | Potential P4 Event - POI 645740_1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-077 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 1 | 137.37 | Potential P4 Event - POI 645740_0 | Cumulative Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-078 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.07424 | 107.44 | 533021 NEOSHO 4 138 533023 N345 3 4 138 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-078 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.07424 | 107.86 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-078 | FROM->TO | 532793 NEOSHO 7 345 997417 N345 TX-1 138 1 | 400 | 440 | 0.05849 | 112.27 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-078 | FROM->TO | 532793 NEOSHO 7 345 997417 N345 TX-1 138 1 | 400 | 440 | 0.05849 | 112.49 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-078 | FROM->TO | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.07424 | 104.96 | 533021 NEOSHO 4 138 533023 N345 3 4 138 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-078 | FROM->TO | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.07424 | 105.16 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-078 | FROM->TO | 533023 N345 3 4 138 997417 N345 TX-1 138 1 | 400 | 440 | 0.05849 | 108.44 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-078 | FROM->TO | 533023 N345 3 4 138 997417 N345 TX-1 138 1 | 400 | 440 | 0.05849 | 108.51 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-078 | FROM->TO | 547467 ORO110 5 161 547469 RIV4525 161 1 | 404 | 420 | 0.07278 | 106.9 | 547469 RIV4525 161 547498 STL439 5 161 1 | Cumulative Impact | ORO11505 to RIV4525 Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-078 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 1 | 123.27 | Potential P4 Event - POI 645740_1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-078 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 1 | 137.37 | Potential P4 Event - POI 645740_0 | Cumulative Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-079 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.07424 | 107.44 | 533021 NEOSHO 4 138 533023 N345 3 4 138 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-079 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.07424 | 107.86 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-079 | FROM->TO | 532793 NEOSHO 7 345 997417 N345 TX-1 138 1 | 400 | 440 | 0.05849 | 112.27 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-079 | FROM->TO | 532793 NEOSHO 7 345 997417 N345 TX-1 138 1 | 400 | 440 | 0.05849 | 112.49 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-079 | FROM->TO | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.07424 | 104.96 | 533021 NEOSHO 4 138 533023 N345 3 4 138 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-079 | FROM->TO | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.07424 | 105.16 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-079 | FROM->TO | 533023 N345 3 4 138 997417 N345 TX-1 138 1 | 400 | 440 | 0.05849 | 108.44 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-079 | FROM->TO | 533023 N345 3 4 138 997417 N345 TX-1 138 1 | 400 | 440 | 0.05849 | 108.51 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-079 | FROM->TO | 547467 ORO110 5 161 547469 RIV4525 161 1 | 404 | 420 | 0.07278 | 106.9 | 547469 RIV4525 161 547498 STL439 5 161 1 | Cumulative Impact | ORO11505 to RIV4525 Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-079 | FROM->TO | 645455 S3455 3 345 645740 S3740 3 345 1 | 1195 | 1195 | 1 | 123.27 | Potential P4 Event - POI 645740_1 | Cumulative Impact | Line - S3454 - S3740 345 kV
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-079 | FROM->TO | 645458 S3458 3 345 645740 S3740 3 345 1 | 1073 | 1073 | 1 | 137.37 | Potential P4 Event - POI 645740_0 | Cumulative Impact | S3458 to S3740 345 kV Ckt 2 New Line
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-183 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.07075 | 107.44 | 533021 NEOSHO 4 138 533023 N345 3 4 138 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-183 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.07075 | 107.86 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-183 | FROM->TO | 532793 NEOSHO 7 345 997417 N345 TX-1 138 1 | 400 | 440 | 0.05476 | 112.27 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-183 | FROM->TO | 532793 NEOSHO 7 345 997417 N345 TX-1 138 1 | 400 | 440 | 0.05476 | 112.49 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-183 | FROM->TO | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.07075 | 104.96 | 533021 NEOSHO 4 138 533023 N345 3 4 138 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-183 | FROM->TO | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.07075 | 105.16 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-183 | FROM->TO | 533023 N345 3 4 138 997417 N345 TX-1 138 1 | 400 | 440 | 0.05476 | 108.44 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-183 | FROM->TO | 533023 N345 3 4 138 997417 N345 TX-1 138 1 | 400 | 440 | 0.05476 | 108.51 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-183 | FROM->TO | 547467 ORO110 5 161 547469 RIV4525 161 1 | 404 | 420 | 0.08431 | 106.9 | 547469 RIV4525 161 547498 STL439 5 161 1 | Cumulative Impact | ORO11505 to RIV4525 Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-204 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.05934 | 107.44 | 533021 NEOSHO 4 138 533023 N345 3 4 138 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-204 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.05934 | 107.86 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-204 | FROM->TO | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.05934 | 104.96 | 533021 NEOSHO 4 138 533023 N345 3 4 138 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-204 | FROM->TO | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.05934 | 105.16 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-204 | FROM->TO | 547467 ORO110 5 161 547469 RIV4525 161 1 | 404 | 420 | 0.07213 | 106.9 | 547469 RIV4525 161 547498 STL439 5 161 1 | Cumulative Impact | ORO11505 to RIV4525 Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.07561 | 107.44 | 533021 NEOSHO 4 138 533023 N345 3 4 138 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.07561 | 107.86 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 532793 NEOSHO 7 345 997417 N345 TX-1 138 1 | 400 | 440 | 0.05951 | 112.27 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 532793 NEOSHO 7 345 997417 N345 TX-1 138 1 | 400 | 440 | 0.05951 | 112.49 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.07561 | 104.96 | 533021 NEOSHO 4 138 533023 N345 3 4 138 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.07561 | 105.16 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 533023 N345 3 4 138 997417 N345 TX-1 138 1 | 400 | 440 | 0.05951 | 108.44 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 533023 N345 3 4 138 997417 N345 TX-1 138 1 | 400 | 440 | 0.05951 | 108.51 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 547467 ORO110 5 161 547469 RIV4525 161 1 | 404 | 420 | 0.07444 | 106.9 | 547469 RIV4525 161 547498 STL439 5 161 1 | Cumulative Impact | ORO11505 to RIV4525 Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | 193 | 193 | 0.27292 | 137.22 | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 193 | 193 | 0.22846 | 100.54 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 193 | 193 | 0.27408 | 137.79 | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.16821 | 127.6 | P13:115-230:SUNC:CONCORDIA_XFR:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17196 | 126.44 | 532765 HOYT 7 345 3WXFMR HOYT1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1721 | 126.94 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17213 | 126.66 | P42:345:OKGE:SB_RARD7381:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17213 | 128.85 | Potential P4 Event - POI 515576_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.26 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.27 | P12:115:OTP:AUTO-SINGLE:BAGLEY7:CLEARBR7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.28 | 659311 PAHOJA__-BE4 230 659735 CLEVELND-LO4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.37 | 655848 BERG -MK7 115 655873 BBCOMPTP-MK7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.37 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.37 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.39 | 655873 BBCOMPTP-MK7 115 659388 KUMMERDG-MK7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.44 | P11:345:GRDA:GRECCTG_1:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.45 | P12:115:XEL:AUTO-SINGLE:NSSTAP7:NSSTL7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.45 | P21:115:XEL:AUTO-SINGLE:NSSTAP7:NSSTL7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.5 | P12:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.5 | P21:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.51 | 505488 CARTHAG5 161 773201 GEN-2023-061 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.53 | 336183 6STCHAR 1A 230 336186 1J396SCPS 1A 21.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.54 | 506944 CHAMSPR5 161 776241 GEN-2023-213 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.55 | 512635 KERR GR5 161 773081 GEN-2023-055 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.55 | 514861 MUSTANG4 138 762614 GEN-2018-026 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.55 | P21:115:XEL:AUTO-SINGLE:REDROCK7:NSSJCT7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.57 | 526936 YOAKUM 7 345 763516 GEN-2019-011 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.62 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.63 | 505522 VAN BUR5 161 773101 GEN-2023-056 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.64 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.73 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.74 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.75 | 640230 HOSK.T89 34.5 640227 HOSKINS4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.76 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.76 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.78 | P12:345:OKGE-OMPA:BKRBKR357_5:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.82 | 509782 R.S.S.-7 345 588040 G16133G16146 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.84 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.84 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.87 | 512749 PAWNSW4 138 773121 GEN-2023-057 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.88 | P12:138:AEPW:ARSHILL4:STLGENS4::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.97 | 640112 CLATONA9 34.5 3WXFMR CLATONIA T1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.99 | P13:161-22:AEPW:FLINTCR5:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.03 | 514922 CLASSEN4 138 775341 GEN-2023-168 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.18 | P12:161:GRDA:SALINA 5-SALNCRK5:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.21 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.21 | P13:345:GRDA:GRDA2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.25 | P11:EHV:EES::1DUKE HS S1:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.27 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.27 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.27 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.28 | P13:138-24:AEPW:TURK 4:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.3 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.31 | P11:16:EES-EAI:MAGNET:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.31 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.33 | 525481 PLANT_X 6 230 774821 GEN-2023-142 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.39 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.41 | 515156 WASHPRK4 138 775321 GEN-2023-167 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.44 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.45 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.47 | 532793 NEOSHO 7 345 765350 GEN-2021-006 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.47 | P23:500:EES-EAI:WH_BLF:B7942 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.48 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.53 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.57 | 515852 DGRASSE7 345 776821 GEN-2023-102 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.61 | 532794 ROSEHIL7 345 773441 GEN-2023-073 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.67 | 776061 GEN-2023-204 345 776064 G23-204GEN1 23.5 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.74 | 773700 G23-086-TAP 230 773701 GEN-2023-086 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.74 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.75 | 515576 RANCHRD7 345 763069 G18-071-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.75 | 763065 GEN-2018-071 345 763069 G18-071-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.8 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.88 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.16 | P11:HV:EES::1RVR_BND_G1!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.16 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.16 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.16 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.27 | 515800 GRACMNT7 345 775261 GEN-2023-164 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.27 | 525832 TUCO_INT 7 345 769921 GEN-2022-147 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.3 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.34 | 525832 TUCO_INT 7 345 525850 ELK_CT1 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.35 | 527000 GAINES_PLNT7 345 527020 SIDEWINDER 7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.36 | GEN-2020-065_POI_527020_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.37 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.37 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.37 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.39 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.63 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.63 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.66 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.73 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.73 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 128.23 | 776060 G23-204-TAP 345 776061 GEN-2023-204 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 128.23 | GEN-2023-204_POI_776060_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 128.42 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 128.64 | Potential P4 Event - POI 337561_27 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 129.52 | Potential P4 Event - POI 525832_3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 131.41 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 131.58 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 144.07 | 772201 GEN-2023-011 115 772202 G23-011XFMR1 34.5 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 144.07 | GEN-2023-011_POI_640208_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17216 | 125.28 | 345439 5PENOCRK 161 345499 5PIKE 1 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17216 | 125.61 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17216 | 125.64 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17216 | 131.43 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17217 | 125.94 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17218 | 125.92 | P12:345:XEL:AUTO-SINGLE:HELENA3:SHEASLK3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17218 | 125.92 | P12:345:XEL:AUTO-SINGLE:WILMART3:SHEASLK3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17218 | 125.94 | P23:345:XEL:8S72 HNA | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1722 | 125.68 | P12:345:MEC:AUTO-SINGLE:OBRIEN3:HIGHLND3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17221 | 126.04 | P42:500:OKGE:SB_FTTH8581:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17221 | 126.04 | P42:500:OKGE:SB_FTTH8585:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17221 | 126.06 | P12:500:OKGE-EESAR:OKGE-EESEAI:BKRBKR317::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17222 | 126.19 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17225 | 125.9 | P12:345:MEC:AUTO-SINGLE:OVRLND3:FALLOW3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17225 | 125.9 | P21:345:MEC:AUTO-SINGLE:OVRLND3:FALLOW3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17225 | 126.48 | 635580 ARBOR HILL 3 345 635590 FALLOW AVE 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17225 | 126.88 | 635580 ARBOR HILL 3 345 635622 RCCN TRL 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17227 | 125.63 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17237 | 126.38 | P23:345:WERE:JEC-345-16:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17239 | 126.26 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17239 | 126.55 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17239 | 126.55 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17239 | 126.55 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17239 | 126.55 | P23:345:MEC:BONDURANT 906 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17239 | 126.55 | P23:345:MEC:BONDURANT:903::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17239 | 126.55 | P23:345:MEC:BONDURANT:906::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17239 | 126.55 | P23:345:MEC:GDMEC 901 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17239 | 126.55 | P23:345:MEC:GDMEC 902 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17239 | 127.14 | P23:345:MEC:MONTEZUMA:902::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17281 | 128.21 | 541197 MULLNCR7 345 771140 G22-208-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17281 | 128.22 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17281 | 128.25 | 541197 MULLNCR7 345 541510 HOLT 7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17281 | 128.26 | Potential P4 Event - POI 541510_1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17287 | 129.59 | Potential P4 Event - POI 532772_9 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1731 | 129.37 | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17311 | 131.76 | 532913 KELLY 5 161 3WXFMR KELL TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17332 | 130.25 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17332 | 130.25 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17518 | 134.72 | P12:161:WERE:TECH-KELL-OPPD-161:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17699 | 135.27 | P21:161:OPPD:S1399-KELLY:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.177 | 135.05 | P21:161:OPPD:HUMBOLT-S1398:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17749 | 134.55 | Potential P4 Event - POI 640590_7 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17749 | 134.55 | Potential P4 Event - POI 640590_8 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17878 | 128.28 | Potential P4 Event - POI 640271_1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.18703 | 149.87 | Potential P4 Event - POI 640590_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.20001 | 143.13 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.20001 | 144.87 | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.20001 | 145.42 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.2342 | 162.09 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.2342 | 163.84 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.2342 | 164.05 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.26649 | 183.26 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640076 BEATRCE7 115 640361 STEINER7 115 1 | 121 | 121 | 0.18013 | 105.68 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.29854 | 136.05 | GEN-2023-225_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31064 | 134.96 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31099 | 135.29 | Potential P4 Event - POI 640226_4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31102 | 134.53 | P45:345:OPPD:S3456-S3458&CBL:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31107 | 134.63 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31109 | 134.66 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31111 | 134.8 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31111 | 135.93 | Potential P4 Event - POI 640226_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31111 | 136.15 | P23:345:MEC:CBEC 905 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31112 | 134.69 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31113 | 134.46 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31113 | 134.48 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31113 | 134.49 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31113 | 134.97 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31113 | 134.97 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31113 | 135.14 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31113 | 135.45 | Potential P4 Event - POI 640226_3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31113 | 135.88 | Potential P4 Event - POI 645740_2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.03 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.19 | 514823 ROMNOSE4 138 775201 GEN-2023-161 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.19 | 515150 CANEYCK4 138 769841 GEN-2022-143 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.2 | 520893 EL RENO4 138 588720 GEN-2017-117 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.21 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.21 | 514787 DEWEY 4 138 766160 GEN-2021-098 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.21 | 520860 COLBERT4 138 769701 GEN-2022-136 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.22 | 515055 MAUD 4 138 771742 G22-238XFMR1 34.5 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.23 | 301643 FOXTROTGSU 34.5 3WXFMR FOXTROTGSU 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.23 | 523823 CARPENTER 7 345 764980 GEN-2020-008 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.23 | 526936 YOAKUM 7 345 766120 GEN-2021-090 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.23 | 655840 CHRRYCRK-MK7 115 655876 DPLWCTAP-MK7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.23 | 655846 F9______-MK7 115 655888 BANKS -MK7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.23 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.23 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.24 | 345831 4TAUM S 1 138 345832 1TAUM S G1 13.8 G1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.24 | 508359 WELSH 7 345 765660 GEN-2021-038 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.24 | 523267 PRINGLE 6 230 774441 GEN-2023-123 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.24 | 523309 MOORE_CNTY 6 230 772181 GEN-2023-010 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.24 | 655882 GALAXYTP-MK7 115 655884 DEMCKSLK-MK7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.44 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.44 | 512650 GRDA1 7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.45 | 511560 GRADY 4 138 511567 CHOCTAW4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.45 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.46 | P12:HV:EES::4SCOTT_1!:4BLOOMFLD%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.47 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.47 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.47 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.49 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.53 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.53 | P12:161:OKGE:BKRBKR197:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.57 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.57 | P12:161:AEPW-SWPA:BEAVER5:EROGERS5::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.57 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.57 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.58 | P12:HV:EES::6DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.59 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.59 | P21:161:ALTW:AUTO-SINGLE:CRYSTLK5:CLKREACT5:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.59 | P21:161:ALTW:AUTO-SINGLE:LIMECKL15:CLKREACT5:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.59 | P23:500:EES:PERVIL:R9872 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.59 | P23:500:EMI:ABF_PRYVL-A | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.59 | P23:500:EMI:ABF_PRYVL-B | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.6 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.6 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.61 | P12:161:AEPW:DYESS5:ELMSPRNG:TONTITN5:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.61 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.61 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.62 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.62 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.64 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.67 | 640119 COL.COG7 115 640028 COLCOG1G 13.8 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.69 | 51993 J2199 SUB 345 3WXFMR J2199 SUB 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.74 | P13:230:UMZW:# 5137 #:: OA IN SD. FAULT ON TRANSFORMER (4).:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.75 | 620322 BSSOUTH4 230 621317 CROWN CAP 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.75 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.77 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.79 | P13:RU901T | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.82 | P13:PR901T GSU | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.82 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.84 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.85 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.85 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.86 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.86 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.88 | P21:345:XEL:AUTO-SINGLE:WILMART3:MEC-345:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.9 | P23:345:OTP::TWIN BRKS 3:BRKY_V2021:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.91 | P11:18:SPC:PR#1:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.95 | P11:024:DPC:ALMA2:6 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.99 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.99 | P12:138:OKGE:BKRBKR130:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.14 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.26 | P23:345:XEL:8P2 KING | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.27 | P11:18:SPC: BD #6+SSL:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.31 | 645740 S3740 3 345 773564 G23-079GEN1 20.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.31 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.35 | P11:18:SPC: BD #6:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.43 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.47 | GEN-2021-043_POI_650290_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.48 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.5 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.5 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.5 | P23:345:XEL:8N17 SHC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.5 | P23:345:XEL:8N22 SHC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.52 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.54 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.55 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.58 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.58 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.71 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.84 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.93 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.04 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.05 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.06 | P23:345:MEC:CBEC 908 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.07 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.13 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.17 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.22 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.22 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.22 | Potential P4 Event - POI 640590_11 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.22 | Potential P4 Event - POI 640590_13 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.28 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.3 | Potential P4 Event - POI 659333_5 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.5 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.52 | Potential P4 Event - POI 645740_12 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.9 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 138.13 | GEN-2023-224_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 138.13 | Potential P4 Event - POI 640590_9 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 141.62 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31115 | 134.61 | 542980 NASHUA 7 345 542982 IATAN 7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31115 | 134.75 | P12:345:OKGE:BKRBKR357_1:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31116 | 134.67 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31117 | 134.57 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31118 | 134.83 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31119 | 134.58 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31203 | 135.9 | P21:161:OPPD:HUMBOLT-S1398:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31203 | 135.91 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31247 | 135.01 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31247 | 135.12 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31523 | 136.4 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31523 | 136.49 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31597 | 136.54 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31597 | 137.27 | P12:115:WERE:KNOB-MKEC-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31597 | 137.29 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.32881 | 148.17 | P12:115:WERE:KNOB-NPPD-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34895 | 153.08 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34895 | 153.08 | P13:115-161:NPPD:HUMBOLT5:T2::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34895 | 154.9 | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34895 | 155.51 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34895 | 155.52 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.37252 | 166.49 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.55338 | 242.37 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.38588 | 127.16 | GEN-2023-225_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40152 | 126.11 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40197 | 126.43 | Potential P4 Event - POI 640226_4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40208 | 125.8 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4021 | 125.83 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40213 | 125.97 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40213 | 127.04 | Potential P4 Event - POI 640226_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40213 | 127.26 | P23:345:MEC:CBEC 905 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40214 | 125.86 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40215 | 125.65 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40215 | 126.58 | Potential P4 Event - POI 640226_3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.64 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.65 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.67 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.74 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.76 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.76 | P23:500:EES:PERVIL:R9872 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.76 | P23:500:EMI:ABF_PRYVL-A | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.76 | P23:500:EMI:ABF_PRYVL-B | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.77 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.79 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.79 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 126.12 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 126.13 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 126.28 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 126.99 | Potential P4 Event - POI 645740_2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.23 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.36 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.36 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.37 | 509895 T.NO.2-4 138 762636 GEN-2018-028 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.38 | 508286 CAMPCOR4 138 765980 GEN-2021-075 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.38 | 508563 PIRKEY 7 345 769761 GEN-2022-139 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.38 | 514823 ROMNOSE4 138 775201 GEN-2023-161 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.38 | 515150 CANEYCK4 138 769841 GEN-2022-143 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.38 | 525830 TUCO_INT 6 230 525840 ANTELOPE_1 6 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.38 | 526299 LUBBCK_EST 6 230 764875 GEN-2020-060 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.39 | 520893 EL RENO4 138 588720 GEN-2017-117 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.4 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.4 | 514787 DEWEY 4 138 766160 GEN-2021-098 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.4 | 520860 COLBERT4 138 769701 GEN-2022-136 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.4 | 655882 GALAXYTP-MK7 115 659388 KUMMERDG-MK7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.41 | 515055 MAUD 4 138 771742 G22-238XFMR1 34.5 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.41 | 655846 F9______-MK7 115 655872 G9TAP___-MK7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.42 | 523823 CARPENTER 7 345 764980 GEN-2020-008 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.42 | 525481 PLANT_X 6 230 775501 GEN-2023-176 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.42 | 655836 OAKDALE -MK7 115 655853 BEARCREK-MK7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.42 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.42 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.62 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.63 | 511560 GRADY 4 138 511567 CHOCTAW4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.64 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.64 | P12:HV:EES::4SCOTT_1!:4BLOOMFLD%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.65 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.67 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.7 | P12:161:AEPW:EROGERS5:ECNTRTN5::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.7 | P12:161:OKGE:BKRBKR197:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.71 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.74 | P12:161:AEPW-SWPA:BEAVER5:EROGERS5::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.74 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.75 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.75 | P12:HV:EES::6DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.76 | P21:161:ALTW:AUTO-SINGLE:CRYSTLK5:CLKREACT5:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.76 | P21:161:ALTW:AUTO-SINGLE:LIMECKL15:CLKREACT5:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.77 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.78 | P12:161:AEPW:DYESS5:ELMSPRNG:TONTITN5:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.78 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.78 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.81 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.84 | 640119 COL.COG7 115 640028 COLCOG1G 13.8 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.85 | 51993 J2199 SUB 345 3WXFMR J2199 SUB 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.9 | P13:230:UMZW:# 5137 #:: OA IN SD. FAULT ON TRANSFORMER (4).:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.92 | 620322 BSSOUTH4 230 621317 CROWN CAP 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.92 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.93 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.95 | P13:RU901T | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.98 | P13:PR901T GSU | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.98 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.01 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.01 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.02 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.02 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.04 | P21:345:XEL:AUTO-SINGLE:WILMART3:MEC-345:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.06 | P23:345:OTP::TWIN BRKS 3:BRKY_V2021:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.11 | P11:024:DPC:ALMA2:6 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.15 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.15 | P12:138:OKGE:BKRBKR130:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.29 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.4 | P23:345:XEL:8P2 KING | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.45 | 645740 S3740 3 345 773564 G23-079GEN1 20.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.45 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.6 | GEN-2021-043_POI_650290_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.61 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.63 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.63 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.63 | P23:345:XEL:8N17 SHC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.63 | P23:345:XEL:8N22 SHC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.65 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.67 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.83 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.95 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.04 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.15 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.16 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.17 | P23:345:MEC:CBEC 908 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.18 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.23 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.27 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.32 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.32 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.32 | Potential P4 Event - POI 640590_11 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.32 | Potential P4 Event - POI 640590_13 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.38 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.39 | Potential P4 Event - POI 659333_5 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.59 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.61 | Potential P4 Event - POI 645740_12 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.97 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 129.14 | GEN-2023-224_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 129.15 | Potential P4 Event - POI 640590_9 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 132.48 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40218 | 125.78 | 542980 NASHUA 7 345 542982 IATAN 7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40219 | 125.84 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40219 | 125.92 | P12:345:OKGE:BKRBKR357_1:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4022 | 125.74 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40222 | 125.99 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40223 | 125.75 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40332 | 127.02 | P21:161:OPPD:HUMBOLT-S1398:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40332 | 127.03 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40388 | 126.16 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40388 | 126.27 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40746 | 127.49 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40746 | 127.58 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40841 | 127.63 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40841 | 128.33 | P12:115:WERE:KNOB-MKEC-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40841 | 128.34 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.42501 | 138.75 | P12:115:WERE:KNOB-NPPD-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45104 | 143.46 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45104 | 145.8 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45104 | 145.81 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4815 | 156.31 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60812 | 189.98 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60812 | 192.94 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60812 | 193.15 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.4 | 771999 G23-222-POI 345 776422 G23-222XFMR1 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.4 | 771999 G23-222-POI 345 776425 G23-222XFMR2 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.4 | 771999 G23-222-POI 345 776442 G23-223XFMR1 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.4 | 776422 G23-222XFMR1 345 776424 G23-222GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.4 | 776425 G23-222XFMR2 345 776427 G23-222GEN2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.4 | GEN-2023-223_POI_771999_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.14 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.54 | 772201 GEN-2023-011 115 772202 G23-011XFMR1 34.5 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.54 | GEN-2023-011_POI_640208_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.59 | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.6 | 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.61 | 640208 HARBINE7 115 640426 STEELEC7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.61 | Potential P4 Event - POI 640590_3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.62 | Potential P4 Event - POI 640590_7 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.62 | Potential P4 Event - POI 640590_8 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.63 | P13:115-345:NPPD:MONOLITH 3:T1::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.63 | P13:115-345:NPPD:MONOLITH 3:T2::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.63 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.63 | Potential P4 Event - POI 640525_3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.63 | Potential P4 Event - POI 640525_4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.63 | Potential P4 Event - POI 640525_5 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.63 | Potential P4 Event - POI 645740_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.29854 | 133.06 | GEN-2023-225_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31064 | 131.95 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31099 | 132.29 | Potential P4 Event - POI 640226_4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31107 | 131.62 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31109 | 131.65 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31111 | 131.79 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31111 | 132.93 | Potential P4 Event - POI 640226_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31111 | 133.16 | P23:345:MEC:CBEC 905 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31112 | 131.68 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31113 | 131.44 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31113 | 131.46 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31113 | 131.48 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31113 | 131.96 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31113 | 131.96 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31113 | 132.13 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31113 | 132.45 | Potential P4 Event - POI 640226_3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31113 | 132.89 | Potential P4 Event - POI 645740_2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.01 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.17 | 514823 ROMNOSE4 138 775201 GEN-2023-161 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.17 | 515150 CANEYCK4 138 769841 GEN-2022-143 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.18 | 520893 EL RENO4 138 588720 GEN-2017-117 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.19 | 514787 DEWEY 4 138 766160 GEN-2021-098 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.19 | 520860 COLBERT4 138 769701 GEN-2022-136 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.21 | 301643 FOXTROTGSU 34.5 3WXFMR FOXTROTGSU 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.21 | 523267 PRINGLE 6 230 774441 GEN-2023-123 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.21 | 523309 MOORE_CNTY 6 230 772181 GEN-2023-010 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.21 | 523823 CARPENTER 7 345 764980 GEN-2020-008 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.21 | 526936 YOAKUM 7 345 766120 GEN-2021-090 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.21 | 655840 CHRRYCRK-MK7 115 655876 DPLWCTAP-MK7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.21 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.21 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.22 | 345831 4TAUM S 1 138 345832 1TAUM S G1 13.8 G1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.22 | 345840 4TAUM S 2 138 345841 1TAUM S G2 13.8 G2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.22 | 508359 WELSH 7 345 765660 GEN-2021-038 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.22 | 532772 STRANGR7 345 3WXFMR STRANGR TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.22 | 655876 DPLWCTAP-MK7 115 655877 LITTLMS4-MK7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.22 | 655882 GALAXYTP-MK7 115 655884 DEMCKSLK-MK7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.42 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.42 | 512650 GRDA1 7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.43 | 511560 GRADY 4 138 511567 CHOCTAW4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.43 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.44 | P12:HV:EES::4SCOTT_1!:4BLOOMFLD%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.45 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.46 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.46 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.48 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.51 | P12:161:AEPW:EROGERS5:ECNTRTN5::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.52 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.52 | P12:161:OKGE:BKRBKR197:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.56 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.56 | P12:161:AEPW-SWPA:BEAVER5:EROGERS5::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.56 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.56 | P12:HV:EES::6DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.56 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.58 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.58 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.58 | P21:161:ALTW:AUTO-SINGLE:CRYSTLK5:CLKREACT5:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.58 | P21:161:ALTW:AUTO-SINGLE:LIMECKL15:CLKREACT5:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.58 | P23:500:EES:PERVIL:R9872 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.58 | P23:500:EMI:ABF_PRYVL-A | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.59 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.59 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.6 | P12:161:AEPW:DYESS5:ELMSPRNG:TONTITN5:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.6 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.6 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.6 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.6 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.62 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.65 | 640119 COL.COG7 115 640028 COLCOG1G 13.8 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.67 | 51993 J2199 SUB 345 3WXFMR J2199 SUB 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.73 | P13:230:UMZW:# 5137 #:: OA IN SD. FAULT ON TRANSFORMER (4).:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.74 | 620322 BSSOUTH4 230 621317 CROWN CAP 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.74 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.76 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.78 | P13:RU901T | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.81 | P13:PR901T GSU | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.81 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.83 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.84 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.84 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.85 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.85 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.87 | P21:345:XEL:AUTO-SINGLE:WILMART3:MEC-345:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.89 | P23:345:OTP::TWIN BRKS 3:BRKY_V2021:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.9 | P11:18:SPC:PR#1:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.95 | P11:024:DPC:ALMA2:6 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.98 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.99 | P12:138:OKGE:BKRBKR130:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.14 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.25 | P23:345:XEL:8P2 KING | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.27 | P11:18:SPC: BD #6+SSL:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.31 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.35 | P11:18:SPC: BD #6:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.43 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.47 | GEN-2021-043_POI_650290_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.48 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.5 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.5 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.5 | P23:345:XEL:8N17 SHC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.5 | P23:345:XEL:8N22 SHC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.52 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.54 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.55 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.58 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.58 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.71 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.84 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.94 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.05 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.07 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.07 | P23:345:MEC:CBEC 908 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.08 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.14 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.18 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.24 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.24 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.24 | Potential P4 Event - POI 640590_10 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.24 | Potential P4 Event - POI 640590_12 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.3 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.31 | Potential P4 Event - POI 659333_5 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.52 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.54 | Potential P4 Event - POI 645740_12 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.93 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 134.78 | 640112 CLATONA9 34.5 3WXFMR CLATONIA T1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 135.18 | GEN-2023-224_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 135.18 | Potential P4 Event - POI 640590_9 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 138.74 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31115 | 131.6 | 542980 NASHUA 7 345 542982 IATAN 7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31115 | 131.74 | P12:345:OKGE:BKRBKR357_1:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31116 | 131.66 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31117 | 131.55 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31118 | 131.82 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31119 | 131.57 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31203 | 132.92 | P21:161:OPPD:HUMBOLT-S1398:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31203 | 132.93 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31247 | 132 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31247 | 132.12 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31523 | 133.41 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31523 | 133.51 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31597 | 133.56 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31597 | 134.31 | P12:115:WERE:KNOB-MKEC-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31597 | 134.32 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.32881 | 145.41 | P12:115:WERE:KNOB-NPPD-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34895 | 150.44 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34895 | 150.44 | P13:115-161:NPPD:HUMBOLT5:T2::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34895 | 152.31 | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34895 | 152.93 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34895 | 152.94 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.37252 | 164.13 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.55338 | 241.55 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.14818 | 100.57 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640234 HUMBOLT5 161 996840 HUMBOLDT T2 115 1 | 126 | 126 | 0.18013 | 101.7 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | 121 | 121 | 0.18013 | 103.74 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.04 | 771999 G23-222-POI 345 776422 G23-222XFMR1 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.04 | 771999 G23-222-POI 345 776425 G23-222XFMR2 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.04 | 771999 G23-222-POI 345 776442 G23-223XFMR1 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.04 | 776422 G23-222XFMR1 345 776424 G23-222GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.04 | 776425 G23-222XFMR2 345 776427 G23-222GEN2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.04 | 776442 G23-223XFMR1 345 776444 G23-223GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.04 | GEN-2023-223_POI_771999_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 171.1 | Potential P4 Event - POI 640590_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 171.12 | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 171.12 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 171.13 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 171.41 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 171.44 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 171.44 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-222 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 171.47 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.07561 | 107.44 | 533021 NEOSHO 4 138 533023 N345 3 4 138 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.07561 | 107.86 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 532793 NEOSHO 7 345 997417 N345 TX-1 138 1 | 400 | 440 | 0.05951 | 112.27 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 532793 NEOSHO 7 345 997417 N345 TX-1 138 1 | 400 | 440 | 0.05951 | 112.49 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.07561 | 104.96 | 533021 NEOSHO 4 138 533023 N345 3 4 138 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.07561 | 105.16 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 533023 N345 3 4 138 997417 N345 TX-1 138 1 | 400 | 440 | 0.05951 | 108.44 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 533023 N345 3 4 138 997417 N345 TX-1 138 1 | 400 | 440 | 0.05951 | 108.51 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 547467 ORO110 5 161 547469 RIV4525 161 1 | 404 | 420 | 0.07444 | 106.9 | 547469 RIV4525 161 547498 STL439 5 161 1 | Cumulative Impact | ORO11505 to RIV4525 Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | 193 | 193 | 0.27292 | 137.22 | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 193 | 193 | 0.22846 | 100.54 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 193 | 193 | 0.27408 | 137.79 | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.16821 | 127.6 | P13:115-230:SUNC:CONCORDIA_XFR:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17196 | 126.44 | 532765 HOYT 7 345 3WXFMR HOYT1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1721 | 126.94 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17213 | 126.66 | P42:345:OKGE:SB_RARD7381:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17213 | 128.85 | Potential P4 Event - POI 515576_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.26 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.27 | P12:115:OTP:AUTO-SINGLE:BAGLEY7:CLEARBR7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.28 | 659311 PAHOJA__-BE4 230 659735 CLEVELND-LO4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.37 | 655848 BERG -MK7 115 655873 BBCOMPTP-MK7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.37 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.37 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.39 | 655873 BBCOMPTP-MK7 115 659388 KUMMERDG-MK7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.44 | P11:345:GRDA:GRECCTG_1:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.45 | P12:115:XEL:AUTO-SINGLE:NSSTAP7:NSSTL7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.45 | P21:115:XEL:AUTO-SINGLE:NSSTAP7:NSSTL7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.5 | P12:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.5 | P21:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.51 | 505488 CARTHAG5 161 773201 GEN-2023-061 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.53 | 336183 6STCHAR 1A 230 336186 1J396SCPS 1A 21.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.54 | 506944 CHAMSPR5 161 776241 GEN-2023-213 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.55 | 512635 KERR GR5 161 773081 GEN-2023-055 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.55 | 514861 MUSTANG4 138 762614 GEN-2018-026 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.55 | P21:115:XEL:AUTO-SINGLE:REDROCK7:NSSJCT7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.57 | 526936 YOAKUM 7 345 763516 GEN-2019-011 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.62 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.63 | 505522 VAN BUR5 161 773101 GEN-2023-056 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.64 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.73 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.74 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.75 | 640230 HOSK.T89 34.5 640227 HOSKINS4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.76 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.76 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.78 | P12:345:OKGE-OMPA:BKRBKR357_5:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.82 | 509782 R.S.S.-7 345 588040 G16133G16146 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.84 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.84 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.87 | 512749 PAWNSW4 138 773121 GEN-2023-057 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.88 | P12:138:AEPW:ARSHILL4:STLGENS4::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.97 | 640112 CLATONA9 34.5 3WXFMR CLATONIA T1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 125.99 | P13:161-22:AEPW:FLINTCR5:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.03 | 514922 CLASSEN4 138 775341 GEN-2023-168 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.18 | P12:161:GRDA:SALINA 5-SALNCRK5:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.21 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.21 | P13:345:GRDA:GRDA2:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.25 | P11:EHV:EES::1DUKE HS S1:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.27 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.27 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.27 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.28 | P13:138-24:AEPW:TURK 4:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.3 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.31 | P11:16:EES-EAI:MAGNET:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.31 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.33 | 525481 PLANT_X 6 230 774821 GEN-2023-142 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.39 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.41 | 515156 WASHPRK4 138 775321 GEN-2023-167 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.44 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.45 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.47 | 532793 NEOSHO 7 345 765350 GEN-2021-006 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.47 | P23:500:EES-EAI:WH_BLF:B7942 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.48 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.53 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.57 | 515852 DGRASSE7 345 776821 GEN-2023-102 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.61 | 532794 ROSEHIL7 345 773441 GEN-2023-073 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.67 | 776061 GEN-2023-204 345 776064 G23-204GEN1 23.5 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.74 | 773700 G23-086-TAP 230 773701 GEN-2023-086 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.74 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.75 | 515576 RANCHRD7 345 763069 G18-071-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.75 | 763065 GEN-2018-071 345 763069 G18-071-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.8 | 532773 SUMMIT 7 345 765340 GEN-2021-005 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 126.88 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.16 | P11:HV:EES::1RVR_BND_G1!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.16 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.16 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.16 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.27 | 515800 GRACMNT7 345 775261 GEN-2023-164 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.27 | 525832 TUCO_INT 7 345 769921 GEN-2022-147 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.3 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.34 | 525832 TUCO_INT 7 345 525850 ELK_CT1 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.35 | 527000 GAINES_PLNT7 345 527020 SIDEWINDER 7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.36 | GEN-2020-065_POI_527020_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.37 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.37 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.37 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.39 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.63 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.63 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.66 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.73 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 127.73 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 128.23 | 776060 G23-204-TAP 345 776061 GEN-2023-204 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 128.23 | GEN-2023-204_POI_776060_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 128.42 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 128.64 | Potential P4 Event - POI 337561_27 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 129.52 | Potential P4 Event - POI 525832_3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 131.41 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 131.58 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 144.07 | 772201 GEN-2023-011 115 772202 G23-011XFMR1 34.5 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17215 | 144.07 | GEN-2023-011_POI_640208_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17216 | 125.28 | 345439 5PENOCRK 161 345499 5PIKE 1 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17216 | 125.61 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17216 | 125.64 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17216 | 131.43 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17217 | 125.94 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17218 | 125.92 | P12:345:XEL:AUTO-SINGLE:HELENA3:SHEASLK3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17218 | 125.92 | P12:345:XEL:AUTO-SINGLE:WILMART3:SHEASLK3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17218 | 125.94 | P23:345:XEL:8S72 HNA | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1722 | 125.68 | P12:345:MEC:AUTO-SINGLE:OBRIEN3:HIGHLND3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17221 | 126.04 | P42:500:OKGE:SB_FTTH8581:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17221 | 126.04 | P42:500:OKGE:SB_FTTH8585:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17221 | 126.06 | P12:500:OKGE-EESAR:OKGE-EESEAI:BKRBKR317::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17222 | 126.19 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17225 | 125.9 | P12:345:MEC:AUTO-SINGLE:OVRLND3:FALLOW3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17225 | 125.9 | P21:345:MEC:AUTO-SINGLE:OVRLND3:FALLOW3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17225 | 126.48 | 635580 ARBOR HILL 3 345 635590 FALLOW AVE 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17225 | 126.88 | 635580 ARBOR HILL 3 345 635622 RCCN TRL 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17227 | 125.63 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17237 | 126.38 | P23:345:WERE:JEC-345-16:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17239 | 126.26 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17239 | 126.55 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17239 | 126.55 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17239 | 126.55 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17239 | 126.55 | P23:345:MEC:BONDURANT 906 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17239 | 126.55 | P23:345:MEC:BONDURANT:903::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17239 | 126.55 | P23:345:MEC:BONDURANT:906::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17239 | 126.55 | P23:345:MEC:GDMEC 901 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17239 | 126.55 | P23:345:MEC:GDMEC 902 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17239 | 127.14 | P23:345:MEC:MONTEZUMA:902::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17281 | 128.21 | 541197 MULLNCR7 345 771140 G22-208-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17281 | 128.22 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17281 | 128.25 | 541197 MULLNCR7 345 541510 HOLT 7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17281 | 128.26 | Potential P4 Event - POI 541510_1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17287 | 129.59 | Potential P4 Event - POI 532772_9 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.1731 | 129.37 | 541199 ST JOE 7 345 640139 COOPER 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17311 | 131.76 | 532913 KELLY 5 161 3WXFMR KELL TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17332 | 130.25 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER_1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17332 | 130.25 | P23:345:GMO-KCPL-NPPD:STJOE-R2-5:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17518 | 134.72 | P12:161:WERE:TECH-KELL-OPPD-161:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17699 | 135.27 | P21:161:OPPD:S1399-KELLY:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.177 | 135.05 | P21:161:OPPD:HUMBOLT-S1398:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17749 | 134.55 | Potential P4 Event - POI 640590_7 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17749 | 134.55 | Potential P4 Event - POI 640590_8 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.17878 | 128.28 | Potential P4 Event - POI 640271_1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.18703 | 149.87 | Potential P4 Event - POI 640590_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.20001 | 143.13 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.20001 | 144.87 | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.20001 | 145.42 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.2342 | 162.09 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.2342 | 163.84 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.2342 | 164.05 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.26649 | 183.26 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640076 BEATRCE7 115 640361 STEINER7 115 1 | 121 | 121 | 0.18013 | 105.68 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.29854 | 136.05 | GEN-2023-225_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31064 | 134.96 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31099 | 135.29 | Potential P4 Event - POI 640226_4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31102 | 134.53 | P45:345:OPPD:S3456-S3458&CBL:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31107 | 134.63 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31109 | 134.66 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31111 | 134.8 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31111 | 135.93 | Potential P4 Event - POI 640226_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31111 | 136.15 | P23:345:MEC:CBEC 905 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31112 | 134.69 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31113 | 134.46 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31113 | 134.48 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31113 | 134.49 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31113 | 134.97 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31113 | 134.97 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31113 | 135.14 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31113 | 135.45 | Potential P4 Event - POI 640226_3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31113 | 135.88 | Potential P4 Event - POI 645740_2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.03 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.19 | 514823 ROMNOSE4 138 775201 GEN-2023-161 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.19 | 515150 CANEYCK4 138 769841 GEN-2022-143 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.2 | 520893 EL RENO4 138 588720 GEN-2017-117 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.21 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.21 | 514787 DEWEY 4 138 766160 GEN-2021-098 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.21 | 520860 COLBERT4 138 769701 GEN-2022-136 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.22 | 515055 MAUD 4 138 771742 G22-238XFMR1 34.5 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.23 | 301643 FOXTROTGSU 34.5 3WXFMR FOXTROTGSU 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.23 | 523823 CARPENTER 7 345 764980 GEN-2020-008 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.23 | 526936 YOAKUM 7 345 766120 GEN-2021-090 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.23 | 655840 CHRRYCRK-MK7 115 655876 DPLWCTAP-MK7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.23 | 655846 F9______-MK7 115 655888 BANKS -MK7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.23 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.23 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.24 | 345831 4TAUM S 1 138 345832 1TAUM S G1 13.8 G1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.24 | 508359 WELSH 7 345 765660 GEN-2021-038 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.24 | 523267 PRINGLE 6 230 774441 GEN-2023-123 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.24 | 523309 MOORE_CNTY 6 230 772181 GEN-2023-010 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.24 | 655882 GALAXYTP-MK7 115 655884 DEMCKSLK-MK7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.44 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.44 | 512650 GRDA1 7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.45 | 511560 GRADY 4 138 511567 CHOCTAW4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.45 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.46 | P12:HV:EES::4SCOTT_1!:4BLOOMFLD%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.47 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.47 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.47 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.49 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.53 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.53 | P12:161:OKGE:BKRBKR197:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.57 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.57 | P12:161:AEPW-SWPA:BEAVER5:EROGERS5::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.57 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.57 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.58 | P12:HV:EES::6DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.59 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.59 | P21:161:ALTW:AUTO-SINGLE:CRYSTLK5:CLKREACT5:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.59 | P21:161:ALTW:AUTO-SINGLE:LIMECKL15:CLKREACT5:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.59 | P23:500:EES:PERVIL:R9872 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.59 | P23:500:EMI:ABF_PRYVL-A | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.59 | P23:500:EMI:ABF_PRYVL-B | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.6 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.6 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.61 | P12:161:AEPW:DYESS5:ELMSPRNG:TONTITN5:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.61 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.61 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.62 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.62 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.64 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.67 | 640119 COL.COG7 115 640028 COLCOG1G 13.8 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.69 | 51993 J2199 SUB 345 3WXFMR J2199 SUB 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.74 | P13:230:UMZW:# 5137 #:: OA IN SD. FAULT ON TRANSFORMER (4).:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.75 | 620322 BSSOUTH4 230 621317 CROWN CAP 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.75 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.77 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.79 | P13:RU901T | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.82 | P13:PR901T GSU | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.82 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.84 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.85 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.85 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.86 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.86 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.88 | P21:345:XEL:AUTO-SINGLE:WILMART3:MEC-345:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.9 | P23:345:OTP::TWIN BRKS 3:BRKY_V2021:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.91 | P11:18:SPC:PR#1:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.95 | P11:024:DPC:ALMA2:6 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.99 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 134.99 | P12:138:OKGE:BKRBKR130:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.14 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.26 | P23:345:XEL:8P2 KING | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.27 | P11:18:SPC: BD #6+SSL:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.31 | 645740 S3740 3 345 773564 G23-079GEN1 20.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.31 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.35 | P11:18:SPC: BD #6:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.43 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.47 | GEN-2021-043_POI_650290_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.48 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.5 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.5 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.5 | P23:345:XEL:8N17 SHC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.5 | P23:345:XEL:8N22 SHC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.52 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.54 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.55 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.58 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.58 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.71 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.84 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 135.93 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.04 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.05 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.06 | P23:345:MEC:CBEC 908 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.07 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.13 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.17 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.22 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.22 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.22 | Potential P4 Event - POI 640590_11 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.22 | Potential P4 Event - POI 640590_13 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.28 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.3 | Potential P4 Event - POI 659333_5 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.5 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.52 | Potential P4 Event - POI 645740_12 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 136.9 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 138.13 | GEN-2023-224_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 138.13 | Potential P4 Event - POI 640590_9 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31114 | 141.62 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31115 | 134.61 | 542980 NASHUA 7 345 542982 IATAN 7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31115 | 134.75 | P12:345:OKGE:BKRBKR357_1:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31116 | 134.67 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31117 | 134.57 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31118 | 134.83 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31119 | 134.58 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31203 | 135.9 | P21:161:OPPD:HUMBOLT-S1398:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31203 | 135.91 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31247 | 135.01 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31247 | 135.12 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31523 | 136.4 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31523 | 136.49 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31597 | 136.54 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31597 | 137.27 | P12:115:WERE:KNOB-MKEC-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.31597 | 137.29 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.32881 | 148.17 | P12:115:WERE:KNOB-NPPD-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34895 | 153.08 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34895 | 153.08 | P13:115-161:NPPD:HUMBOLT5:T2::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34895 | 154.9 | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34895 | 155.51 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.34895 | 155.52 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.37252 | 166.49 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 140 | 140 | 0.55338 | 242.37 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.38588 | 127.16 | GEN-2023-225_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40152 | 126.11 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40197 | 126.43 | Potential P4 Event - POI 640226_4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40208 | 125.8 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4021 | 125.83 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40213 | 125.97 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40213 | 127.04 | Potential P4 Event - POI 640226_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40213 | 127.26 | P23:345:MEC:CBEC 905 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40214 | 125.86 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40215 | 125.65 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40215 | 126.58 | Potential P4 Event - POI 640226_3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.64 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.65 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.67 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.74 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.76 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.76 | P23:500:EES:PERVIL:R9872 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.76 | P23:500:EMI:ABF_PRYVL-A | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.76 | P23:500:EMI:ABF_PRYVL-B | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.77 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.79 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 125.79 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 126.12 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 126.13 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 126.28 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40216 | 126.99 | Potential P4 Event - POI 645740_2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.23 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.36 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.36 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.37 | 509895 T.NO.2-4 138 762636 GEN-2018-028 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.38 | 508286 CAMPCOR4 138 765980 GEN-2021-075 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.38 | 508563 PIRKEY 7 345 769761 GEN-2022-139 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.38 | 514823 ROMNOSE4 138 775201 GEN-2023-161 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.38 | 515150 CANEYCK4 138 769841 GEN-2022-143 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.38 | 525830 TUCO_INT 6 230 525840 ANTELOPE_1 6 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.38 | 526299 LUBBCK_EST 6 230 764875 GEN-2020-060 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.39 | 520893 EL RENO4 138 588720 GEN-2017-117 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.4 | 338341 1EAI DELLST3 18.0 338340 8CC_DELL 500 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.4 | 514787 DEWEY 4 138 766160 GEN-2021-098 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.4 | 520860 COLBERT4 138 769701 GEN-2022-136 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.4 | 655882 GALAXYTP-MK7 115 659388 KUMMERDG-MK7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.41 | 515055 MAUD 4 138 771742 G22-238XFMR1 34.5 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.41 | 655846 F9______-MK7 115 655872 G9TAP___-MK7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.42 | 523823 CARPENTER 7 345 764980 GEN-2020-008 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.42 | 525481 PLANT_X 6 230 775501 GEN-2023-176 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.42 | 655836 OAKDALE -MK7 115 655853 BEARCREK-MK7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.42 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.42 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.62 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.63 | 511560 GRADY 4 138 511567 CHOCTAW4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.64 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.64 | P12:HV:EES::4SCOTT_1!:4BLOOMFLD%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.65 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.67 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.7 | P12:161:AEPW:EROGERS5:ECNTRTN5::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.7 | P12:161:OKGE:BKRBKR197:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.71 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.74 | P12:161:AEPW-SWPA:BEAVER5:EROGERS5::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.74 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.75 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.75 | P12:HV:EES::6DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.76 | P21:161:ALTW:AUTO-SINGLE:CRYSTLK5:CLKREACT5:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.76 | P21:161:ALTW:AUTO-SINGLE:LIMECKL15:CLKREACT5:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.77 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.78 | P12:161:AEPW:DYESS5:ELMSPRNG:TONTITN5:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.78 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.78 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.81 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.84 | 640119 COL.COG7 115 640028 COLCOG1G 13.8 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.85 | 51993 J2199 SUB 345 3WXFMR J2199 SUB 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.9 | P13:230:UMZW:# 5137 #:: OA IN SD. FAULT ON TRANSFORMER (4).:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.92 | 620322 BSSOUTH4 230 621317 CROWN CAP 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.92 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.93 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.95 | P13:RU901T | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.98 | P13:PR901T GSU | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 125.98 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.01 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.01 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.02 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.02 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.04 | P21:345:XEL:AUTO-SINGLE:WILMART3:MEC-345:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.06 | P23:345:OTP::TWIN BRKS 3:BRKY_V2021:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.11 | P11:024:DPC:ALMA2:6 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.15 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.15 | P12:138:OKGE:BKRBKR130:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.29 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.4 | P23:345:XEL:8P2 KING | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.45 | 645740 S3740 3 345 773564 G23-079GEN1 20.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.45 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.6 | GEN-2021-043_POI_650290_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.61 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.63 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.63 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.63 | P23:345:XEL:8N17 SHC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.63 | P23:345:XEL:8N22 SHC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.65 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.67 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.83 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 126.95 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.04 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.15 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.16 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.17 | P23:345:MEC:CBEC 908 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.18 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.23 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.27 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.32 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.32 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.32 | Potential P4 Event - POI 640590_11 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.32 | Potential P4 Event - POI 640590_13 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.38 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.39 | Potential P4 Event - POI 659333_5 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.59 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.61 | Potential P4 Event - POI 645740_12 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 127.97 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 129.14 | GEN-2023-224_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 129.15 | Potential P4 Event - POI 640590_9 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40217 | 132.48 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40218 | 125.78 | 542980 NASHUA 7 345 542982 IATAN 7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40219 | 125.84 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40219 | 125.92 | P12:345:OKGE:BKRBKR357_1:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4022 | 125.74 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40222 | 125.99 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40223 | 125.75 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40332 | 127.02 | P21:161:OPPD:HUMBOLT-S1398:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40332 | 127.03 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40388 | 126.16 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40388 | 126.27 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40746 | 127.49 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40746 | 127.58 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40841 | 127.63 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40841 | 128.33 | P12:115:WERE:KNOB-MKEC-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.40841 | 128.34 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.42501 | 138.75 | P12:115:WERE:KNOB-NPPD-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45104 | 143.46 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45104 | 145.8 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.45104 | 145.81 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.4815 | 156.31 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60812 | 189.98 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60812 | 192.94 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 193 | 193 | 0.60812 | 193.15 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.4 | 771999 G23-222-POI 345 776422 G23-222XFMR1 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.4 | 771999 G23-222-POI 345 776425 G23-222XFMR2 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.4 | 776422 G23-222XFMR1 345 776424 G23-222GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 115.4 | 776425 G23-222XFMR2 345 776427 G23-222GEN2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.14 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.54 | 772201 GEN-2023-011 115 772202 G23-011XFMR1 34.5 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.54 | GEN-2023-011_POI_640208_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.59 | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.6 | 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.61 | 640208 HARBINE7 115 640426 STEELEC7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.61 | Potential P4 Event - POI 640590_3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.62 | Potential P4 Event - POI 640590_7 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.62 | Potential P4 Event - POI 640590_8 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.63 | P13:115-345:NPPD:MONOLITH 3:T1::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.63 | P13:115-345:NPPD:MONOLITH 3:T2::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.63 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.63 | Potential P4 Event - POI 640525_3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.63 | Potential P4 Event - POI 640525_4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.63 | Potential P4 Event - POI 640525_5 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 172.63 | Potential P4 Event - POI 645740_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.29854 | 133.06 | GEN-2023-225_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31064 | 131.95 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31099 | 132.29 | Potential P4 Event - POI 640226_4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31107 | 131.62 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31109 | 131.65 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31111 | 131.79 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31111 | 132.93 | Potential P4 Event - POI 640226_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31111 | 133.16 | P23:345:MEC:CBEC 905 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31112 | 131.68 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31113 | 131.44 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31113 | 131.46 | P12:161:AMMO-AECI::THOMASHILL:ADAIR:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31113 | 131.48 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31113 | 131.96 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31113 | 131.96 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31113 | 132.13 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31113 | 132.45 | Potential P4 Event - POI 640226_3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31113 | 132.89 | Potential P4 Event - POI 645740_2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.01 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.17 | 514823 ROMNOSE4 138 775201 GEN-2023-161 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.17 | 515150 CANEYCK4 138 769841 GEN-2022-143 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.18 | 520893 EL RENO4 138 588720 GEN-2017-117 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.19 | 514787 DEWEY 4 138 766160 GEN-2021-098 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.19 | 520860 COLBERT4 138 769701 GEN-2022-136 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.21 | 301643 FOXTROTGSU 34.5 3WXFMR FOXTROTGSU 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.21 | 523267 PRINGLE 6 230 774441 GEN-2023-123 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.21 | 523309 MOORE_CNTY 6 230 772181 GEN-2023-010 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.21 | 523823 CARPENTER 7 345 764980 GEN-2020-008 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.21 | 526936 YOAKUM 7 345 766120 GEN-2021-090 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.21 | 655840 CHRRYCRK-MK7 115 655876 DPLWCTAP-MK7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.21 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.21 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.22 | 345831 4TAUM S 1 138 345832 1TAUM S G1 13.8 G1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.22 | 345840 4TAUM S 2 138 345841 1TAUM S G2 13.8 G2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.22 | 508359 WELSH 7 345 765660 GEN-2021-038 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.22 | 532772 STRANGR7 345 3WXFMR STRANGR TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.22 | 655876 DPLWCTAP-MK7 115 655877 LITTLMS4-MK7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.22 | 655882 GALAXYTP-MK7 115 655884 DEMCKSLK-MK7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.42 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.42 | 512650 GRDA1 7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.43 | 511560 GRADY 4 138 511567 CHOCTAW4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.43 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.44 | P12:HV:EES::4SCOTT_1!:4BLOOMFLD%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.45 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.46 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.46 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.48 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.51 | P12:161:AEPW:EROGERS5:ECNTRTN5::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.52 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.52 | P12:161:OKGE:BKRBKR197:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.56 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.56 | P12:161:AEPW-SWPA:BEAVER5:EROGERS5::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.56 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.56 | P12:HV:EES::6DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.56 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.58 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.58 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.58 | P21:161:ALTW:AUTO-SINGLE:CRYSTLK5:CLKREACT5:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.58 | P21:161:ALTW:AUTO-SINGLE:LIMECKL15:CLKREACT5:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.58 | P23:500:EES:PERVIL:R9872 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.58 | P23:500:EMI:ABF_PRYVL-A | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.59 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.59 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.6 | P12:161:AEPW:DYESS5:ELMSPRNG:TONTITN5:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.6 | P12:500:EES-EAI:ND:8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.6 | P12:EHV:EES::8SANS SOUCI%:8DRIVER%:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.6 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.6 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.62 | 603294 MEC CT2 115 600172 G261 MEC CT2 15.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.65 | 640119 COL.COG7 115 640028 COLCOG1G 13.8 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.67 | 51993 J2199 SUB 345 3WXFMR J2199 SUB 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.73 | P13:230:UMZW:# 5137 #:: OA IN SD. FAULT ON TRANSFORMER (4).:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.74 | 620322 BSSOUTH4 230 621317 CROWN CAP 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.74 | 621317 CROWN CAP 230 621318 CROWN RDG 230 Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.76 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.78 | P13:RU901T | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.81 | P13:PR901T GSU | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.81 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.83 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.84 | 659333 JUDSON__-BE3 345 773921 GEN-2023-097 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.84 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.85 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.85 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.87 | P21:345:XEL:AUTO-SINGLE:WILMART3:MEC-345:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.89 | P23:345:OTP::TWIN BRKS 3:BRKY_V2021:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.9 | P11:18:SPC:PR#1:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.95 | P11:024:DPC:ALMA2:6 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.98 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 131.99 | P12:138:OKGE:BKRBKR130:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.14 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.25 | P23:345:XEL:8P2 KING | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.27 | P11:18:SPC: BD #6+SSL:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.31 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.35 | P11:18:SPC: BD #6:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.43 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.47 | GEN-2021-043_POI_650290_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.48 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.5 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.5 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.5 | P23:345:XEL:8N17 SHC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.5 | P23:345:XEL:8N22 SHC | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.52 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.54 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.55 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.58 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.58 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.71 | 659333 JUDSON__-BE3 345 767161 GEN-2022-009 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.84 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 132.94 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.05 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.07 | 776482 G23-225XFMR1 345 776485 G23-225GSU1 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.07 | P23:345:MEC:CBEC 908 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.08 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.14 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.18 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.24 | 776462 G23-224XFMR1 345 776464 G23-224GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.24 | 776465 G23-224XFMR2 345 776467 G23-224GEN2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.24 | Potential P4 Event - POI 640590_10 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.24 | Potential P4 Event - POI 640590_12 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.3 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.31 | Potential P4 Event - POI 659333_5 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.52 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.54 | Potential P4 Event - POI 645740_12 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 133.93 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 134.78 | 640112 CLATONA9 34.5 3WXFMR CLATONIA T1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 135.18 | GEN-2023-224_POI_640590_Generator_outage | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 135.18 | Potential P4 Event - POI 640590_9 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31114 | 138.74 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31115 | 131.6 | 542980 NASHUA 7 345 542982 IATAN 7 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31115 | 131.74 | P12:345:OKGE:BKRBKR357_1:::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31116 | 131.66 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31117 | 131.55 | 532773 SUMMIT 7 345 3WXFMR SUMMIT TX-1 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31118 | 131.82 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31119 | 131.57 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31203 | 132.92 | P21:161:OPPD:HUMBOLT-S1398:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31203 | 132.93 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31247 | 132 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31247 | 132.12 | 532913 KELLY 5 161 532920 TECHILL5 161 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31523 | 133.41 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31523 | 133.51 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31597 | 133.56 | 539656 CLIFTON3 115 539665 GRNLEAF3 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31597 | 134.31 | P12:115:WERE:KNOB-MKEC-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.31597 | 134.32 | P12:115:SUNC-WERE:CLIFTON-KNOBHILL:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.32881 | 145.41 | P12:115:WERE:KNOB-NPPD-115:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34895 | 150.44 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34895 | 150.44 | P13:115-161:NPPD:HUMBOLT5:T2::: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34895 | 152.31 | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34895 | 152.93 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.34895 | 152.94 | P12:115:NPPD:1176:BEATRCE7-HUMBOLT7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.37252 | 164.13 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 137 | 137 | 0.55338 | 241.55 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.14818 | 100.57 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640234 HUMBOLT5 161 996840 HUMBOLDT T2 115 1 | 126 | 126 | 0.18013 | 101.7 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | 121 | 121 | 0.18013 | 103.74 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.04 | 771999 G23-222-POI 345 776422 G23-222XFMR1 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.04 | 771999 G23-222-POI 345 776425 G23-222XFMR2 345 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.04 | 776422 G23-222XFMR1 345 776424 G23-222GEN1 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 114.04 | 776425 G23-222XFMR2 345 776427 G23-222GEN2 18.0 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 171.1 | Potential P4 Event - POI 640590_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 171.12 | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 171.12 | P13:115-161:NPPD:HUMBOLDT T2:::HV: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 171.13 | 640076 BEATRCE7 115 640361 STEINER7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 171.41 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 171.44 | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 171.44 | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-223 | FROM->TO | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 417 | 417 | 1 | 171.47 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-224 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.07483 | 107.44 | 533021 NEOSHO 4 138 533023 N345 3 4 138 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-224 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.07483 | 107.86 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-224 | FROM->TO | 532793 NEOSHO 7 345 997417 N345 TX-1 138 1 | 400 | 440 | 0.05891 | 112.27 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-224 | FROM->TO | 532793 NEOSHO 7 345 997417 N345 TX-1 138 1 | 400 | 440 | 0.05891 | 112.49 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-224 | FROM->TO | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.07483 | 104.96 | 533021 NEOSHO 4 138 533023 N345 3 4 138 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-224 | FROM->TO | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.07483 | 105.16 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-224 | FROM->TO | 533023 N345 3 4 138 997417 N345 TX-1 138 1 | 400 | 440 | 0.05891 | 108.44 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-224 | FROM->TO | 533023 N345 3 4 138 997417 N345 TX-1 138 1 | 400 | 440 | 0.05891 | 108.51 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-224 | FROM->TO | 547467 ORO110 5 161 547469 RIV4525 161 1 | 404 | 420 | 0.07375 | 106.9 | 547469 RIV4525 161 547498 STL439 5 161 1 | Cumulative Impact | ORO11505 to RIV4525 Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-224 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.05939 | 149.87 | Potential P4 Event - POI 640590_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-225 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.07483 | 107.44 | 533021 NEOSHO 4 138 533023 N345 3 4 138 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-225 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.07483 | 107.86 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-225 | FROM->TO | 532793 NEOSHO 7 345 997417 N345 TX-1 138 1 | 400 | 440 | 0.05891 | 112.27 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-225 | FROM->TO | 532793 NEOSHO 7 345 997417 N345 TX-1 138 1 | 400 | 440 | 0.05891 | 112.49 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-225 | FROM->TO | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.07483 | 104.96 | 533021 NEOSHO 4 138 533023 N345 3 4 138 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-225 | FROM->TO | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.07483 | 105.16 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-225 | FROM->TO | 533023 N345 3 4 138 997417 N345 TX-1 138 1 | 400 | 440 | 0.05891 | 108.44 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-225 | FROM->TO | 533023 N345 3 4 138 997417 N345 TX-1 138 1 | 400 | 440 | 0.05891 | 108.51 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-225 | FROM->TO | 547467 ORO110 5 161 547469 RIV4525 161 1 | 404 | 420 | 0.07375 | 106.9 | 547469 RIV4525 161 547498 STL439 5 161 1 | Cumulative Impact | ORO11505 to RIV4525 Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 00ALL | 1 | 27WP | GEN-2023-225 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.05939 | 149.87 | Potential P4 Event - POI 640590_0 | Cumulative Impact | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23918 | 108.48 | System-Intact | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23918 | 102.93 | System-Intact | TDF Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.03918 | 133.83 | System-Intact | TDF Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 143.24 | System-Intact | TDF Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 133.83 | System-Intact | TDF Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 155.54 | System-Intact | TDF Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 160.18 | System-Intact | TDF Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-035 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.03758 | 124.12 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-038 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.03127 | 124.12 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 143.24 | System-Intact | TDF Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 133.83 | System-Intact | TDF Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 155.54 | System-Intact | TDF Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 160.18 | System-Intact | TDF Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 143.24 | System-Intact | TDF Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 133.83 | System-Intact | TDF Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 155.54 | System-Intact | TDF Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 160.18 | System-Intact | TDF Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-057 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.06269 | 124.12 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-088 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.03122 | 124.12 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-100 | FROM->TO | 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | 1076 | 1076 | 0.03792 | 106.07 | System-Intact | TDF Impact | Rebuild the existing SWISVAL7 to G23-220-TAP 345 kV line; Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-102 | FROM->TO | 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | 1076 | 1076 | 0.03792 | 106.07 | System-Intact | TDF Impact | Rebuild the existing SWISVAL7 to G23-220-TAP 345 kV line; Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.71105 | 109.57 | System-Intact | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-104 | FROM->TO | 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | 1076 | 1076 | 0.03519 | 106.07 | System-Intact | TDF Impact | Rebuild the existing SWISVAL7 to G23-220-TAP 345 kV line; Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-134 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.03331 | 124.12 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-150 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.03437 | 124.12 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-161 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.03375 | 124.12 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-164 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.03402 | 124.12 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-165 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.03402 | 124.12 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-166 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.04689 | 124.12 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-167 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.04495 | 124.12 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-168 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.04521 | 124.12 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-174 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.03611 | 124.12 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-177 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.03585 | 124.12 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-205 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.03035 | 124.12 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-210 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.03912 | 124.12 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | 1076 | 1076 | 0.03913 | 106.07 | System-Intact | TDF Impact | Rebuild the existing SWISVAL7 to G23-220-TAP 345 kV line; Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 124.12 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-229 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.0342 | 124.12 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-022 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.03112 | 119.33 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23902 | 107.61 | System-Intact | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23902 | 102.14 | System-Intact | TDF Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.03875 | 131.48 | System-Intact | TDF Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 141.15 | System-Intact | TDF Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 131.48 | System-Intact | TDF Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 153.26 | System-Intact | TDF Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 158.1 | System-Intact | TDF Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-035 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.03616 | 119.33 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-038 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.03296 | 119.33 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 141.15 | System-Intact | TDF Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 131.48 | System-Intact | TDF Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 153.26 | System-Intact | TDF Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 158.1 | System-Intact | TDF Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 141.15 | System-Intact | TDF Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 131.48 | System-Intact | TDF Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 153.26 | System-Intact | TDF Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 158.1 | System-Intact | TDF Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-056 | FROM->TO | 515336 VBI 2 69.0 997771 VBI2 69.0 2 | 76 | 95 | 0.0403 | 103.63 | System-Intact | TDF Impact | Upgrade the existing VBI2 161/69 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-056 | FROM->TO | 515339 VBI 5 161 997771 VBI2 69.0 2 | 76 | 95 | 0.0403 | 103.84 | System-Intact | TDF Impact | Upgrade the existing VBI2 161/69 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-057 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.06344 | 119.33 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-063 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.03559 | 119.33 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-069 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.03077 | 119.33 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-088 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.03658 | 119.33 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-100 | FROM->TO | 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | 1076 | 1076 | 0.0347 | 104.65 | System-Intact | TDF Impact | Rebuild the existing SWISVAL7 to G23-220-TAP 345 kV line; Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-102 | FROM->TO | 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | 1076 | 1076 | 0.0347 | 104.65 | System-Intact | TDF Impact | Rebuild the existing SWISVAL7 to G23-220-TAP 345 kV line; Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.71107 | 112.35 | System-Intact | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | 1076 | 1076 | 0.03248 | 104.65 | System-Intact | TDF Impact | Rebuild the existing SWISVAL7 to G23-220-TAP 345 kV line; Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-134 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.03729 | 119.33 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-150 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.03298 | 119.33 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-161 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.03157 | 119.33 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-164 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.03237 | 119.33 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-165 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.03237 | 119.33 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-166 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.0449 | 119.33 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-167 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.04339 | 119.33 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-168 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.04334 | 119.33 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-174 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.03556 | 119.33 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-177 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.03614 | 119.33 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-205 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.03569 | 119.33 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-210 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.04088 | 119.33 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | 1076 | 1076 | 0.03474 | 104.65 | System-Intact | TDF Impact | Rebuild the existing SWISVAL7 to G23-220-TAP 345 kV line; Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 119.33 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-229 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.03277 | 119.33 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.03951 | 134.56 | System-Intact | TDF Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 122.77 | System-Intact | TDF Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 134.56 | System-Intact | TDF Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 133.75 | System-Intact | TDF Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 125.83 | System-Intact | TDF Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 122.77 | System-Intact | TDF Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 134.56 | System-Intact | TDF Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 133.75 | System-Intact | TDF Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 125.83 | System-Intact | TDF Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 122.77 | System-Intact | TDF Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 134.56 | System-Intact | TDF Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 133.75 | System-Intact | TDF Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 125.83 | System-Intact | TDF Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-138 | FROM->TO | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | 266 | 273 | 0.03657 | 103.55 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-213 | FROM->TO | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | 266 | 273 | 0.07203 | 103.55 | System-Intact | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-009 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.30474 | 101.11 | P23:345:AEPW:VALLIANT CB 3413A NBTB:::: | TDF Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-009 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.30474 | 101.11 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT:::: | TDF Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-009 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.30696 | 102.47 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-009 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.49466 | 103.89 | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | TDF Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-009 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.49466 | 103.89 | 521157 HUGO 7 345 3WXFMR HUGO 1 1 | TDF Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.22032 | 117.54 | P12:161:AEPW-EMDE:FLINTCR5:739952::: | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.22359 | 108.4 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.22359 | 108.42 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23693 | 109.04 | Potential P4 Event - POI 509745_2 | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23693 | 110.11 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23716 | 108.59 | Potential P4 Event - POI 509745_0 | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23716 | 108.96 | Potential P4 Event - POI 509745_1 | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23922 | 101.29 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23934 | 101.17 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.2394 | 100.18 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.2394 | 103.05 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23941 | 101.53 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23984 | 114.03 | 512650 GRDA1 7 345 774740 G23-138-TAP 345 1 | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23984 | 119.2 | Potential P4 Event - POI 774740_1 | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23984 | 119.3 | Potential P4 Event - POI 774740_2 | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23984 | 119.32 | Potential P4 Event - POI 774740_0 | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23984 | 122.63 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23985 | 113.61 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23985 | 113.83 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23985 | 113.83 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT:::: | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.24021 | 100.5 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.22032 | 112.52 | P12:161:AEPW-EMDE:FLINTCR5:739952::: | TDF Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.22359 | 103.42 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | TDF Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.22359 | 103.44 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | TDF Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23693 | 104.18 | Potential P4 Event - POI 509745_2 | TDF Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23693 | 105.24 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23716 | 103.73 | Potential P4 Event - POI 509745_0 | TDF Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23716 | 104.1 | Potential P4 Event - POI 509745_1 | TDF Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23984 | 109.1 | 512650 GRDA1 7 345 774740 G23-138-TAP 345 1 | TDF Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23984 | 114.19 | Potential P4 Event - POI 774740_1 | TDF Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23984 | 114.27 | Potential P4 Event - POI 774740_2 | TDF Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23984 | 114.29 | Potential P4 Event - POI 774740_0 | TDF Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23984 | 117.57 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | TDF Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23985 | 108.6 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | TDF Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23985 | 108.8 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23985 | 108.8 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT:::: | TDF Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997940 GROVE 138 1 | 112 | 112 | 0.20249 | 102.59 | Potential P4 Event - POI 509745_2 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997940 GROVE 138 1 | 112 | 112 | 0.20249 | 103.63 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997940 GROVE 138 1 | 112 | 112 | 0.20268 | 102.14 | Potential P4 Event - POI 509745_0 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997940 GROVE 138 1 | 112 | 112 | 0.20268 | 102.5 | Potential P4 Event - POI 509745_1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997940 GROVE 138 1 | 112 | 112 | 0.20572 | 108.49 | 512650 GRDA1 7 345 774740 G23-138-TAP 345 1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997940 GROVE 138 1 | 112 | 112 | 0.20572 | 113.59 | Potential P4 Event - POI 774740_0 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997940 GROVE 138 1 | 112 | 112 | 0.20572 | 113.59 | Potential P4 Event - POI 774740_2 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997940 GROVE 138 1 | 112 | 112 | 0.20572 | 113.73 | Potential P4 Event - POI 774740_1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997940 GROVE 138 1 | 112 | 112 | 0.20572 | 117.08 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997940 GROVE 138 1 | 112 | 112 | 0.20577 | 107.19 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997940 GROVE 138 1 | 112 | 112 | 0.20577 | 107.19 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT:::: | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997940 GROVE 138 1 | 112 | 112 | 0.20577 | 107.65 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997940 GROVE 138 1 | 112 | 112 | 0.20249 | 103.83 | Potential P4 Event - POI 509745_2 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997940 GROVE 138 1 | 112 | 112 | 0.20249 | 104.88 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997940 GROVE 138 1 | 112 | 112 | 0.20268 | 103.36 | Potential P4 Event - POI 509745_0 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997940 GROVE 138 1 | 112 | 112 | 0.20268 | 103.73 | Potential P4 Event - POI 509745_1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997940 GROVE 138 1 | 112 | 112 | 0.20572 | 109.68 | 512650 GRDA1 7 345 774740 G23-138-TAP 345 1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997940 GROVE 138 1 | 112 | 112 | 0.20572 | 114.69 | Potential P4 Event - POI 774740_0 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997940 GROVE 138 1 | 112 | 112 | 0.20572 | 114.69 | Potential P4 Event - POI 774740_2 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997940 GROVE 138 1 | 112 | 112 | 0.20572 | 114.89 | Potential P4 Event - POI 774740_1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997940 GROVE 138 1 | 112 | 112 | 0.20572 | 118.27 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997940 GROVE 138 1 | 112 | 112 | 0.20577 | 107.94 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997940 GROVE 138 1 | 112 | 112 | 0.20577 | 107.94 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT:::: | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997940 GROVE 138 1 | 112 | 112 | 0.20577 | 108.51 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | 335 | 335 | 1 | 111.98 | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | TDF Impact | DRYGULCH5 to G23-028-TAP 161 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.30695 | 165.54 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.30444 | 126.84 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.34204 | 180.63 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.34204 | 185.33 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 0.36124 | 101.6 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | TDF Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 113.45 | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | TDF Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 134.05 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | 335 | 335 | 1 | 111.98 | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | TDF Impact | DRYGULCH5 to G23-028-TAP 161 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.30695 | 165.54 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.30444 | 126.84 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.2113 | 169.8 | 512654 PENSA 5 161 3WXFMR PENAUTO1 1 | TDF Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.34204 | 180.63 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.2113 | 174.45 | 512654 PENSA 5 161 3WXFMR PENAUTO1 1 | TDF Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.34204 | 185.33 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 0.47558 | 101.6 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | TDF Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 113.45 | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | TDF Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 134.05 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-075 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.59736 | 103.8 | Potential P4 Event - POI 532794_2 | TDF Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-075 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.60178 | 103.23 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-075 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.60178 | 103.23 | Potential P4 Event - POI 532794_9 | TDF Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-075 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.60179 | 103.44 | Potential P4 Event - POI 532794_5 | TDF Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-075 | FROM->TO | 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | 1015 | 1015 | 0.20042 | 101.92 | Potential P4 Event - POI 532794_7 | TDF Impact | Line - Wolf Creek - Blackberry 345 kV
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-075 | FROM->TO | 767240 G22-013-TAP 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.20042 | 102.19 | Potential P4 Event - POI 532794_7 | TDF Impact | Line - Wolf Creek - Blackberry 345 kV
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-076 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.59736 | 103.8 | Potential P4 Event - POI 532794_2 | TDF Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-076 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.60178 | 103.23 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-076 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.60178 | 103.23 | Potential P4 Event - POI 532794_9 | TDF Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-076 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.60179 | 103.44 | Potential P4 Event - POI 532794_5 | TDF Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-076 | FROM->TO | 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | 1015 | 1015 | 0.20042 | 101.92 | Potential P4 Event - POI 532794_7 | TDF Impact | Line - Wolf Creek - Blackberry 345 kV
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-076 | FROM->TO | 767240 G22-013-TAP 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.20042 | 102.19 | Potential P4 Event - POI 532794_7 | TDF Impact | Line - Wolf Creek - Blackberry 345 kV
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-092 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.26575 | 101.11 | P23:345:AEPW:VALLIANT CB 3413A NBTB:::: | TDF Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-092 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.26575 | 101.11 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT:::: | TDF Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-092 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.26787 | 102.47 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-092 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.42496 | 103.89 | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | TDF Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-092 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.42496 | 103.89 | 521157 HUGO 7 345 3WXFMR HUGO 1 1 | TDF Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 435 | 435 | 1 | 108.76 | 523777 WHEELER 6 230 774000 G23-101-TAP 230 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-101 | FROM->TO | 523777 WHEELER 6 230 774000 G23-101-TAP 230 1 | 353 | 353 | 0.32775 | 100.05 | P12:345:OKGE-AEP:BKRBKR4291:::: | TDF Impact | Rebuild the existing WHEELER 6 to G23-101-TAP 230 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-101 | FROM->TO | 523777 WHEELER 6 230 774000 G23-101-TAP 230 1 | 353 | 353 | 1 | 135.1 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing WHEELER 6 to G23-101-TAP 230 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.68747 | 141.7 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.68747 | 141.7 | Potential P4 Event - POI 515375_23 | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.68747 | 141.7 | Potential P4 Event - POI 515852_0 | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.70671 | 109.01 | Potential P4 Event - POI 515852_8 | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.70671 | 109.02 | Potential P4 Event - POI 515852_4 | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.7068 | 102.56 | Potential P4 Event - POI 515375_27 | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.7068 | 102.56 | Potential P4 Event - POI 515375_36 | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.70944 | 107.72 | P42:345:OKGE:SB_REOW7312:::: | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.70944 | 107.72 | Potential P4 Event - POI 515543_0 | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.70957 | 107.01 | P12:345:OKGE:BKRBKR421:::: | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.70957 | 107.86 | Potential P4 Event - POI 515543_1 | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.70998 | 106.64 | Potential P4 Event - POI 514715_2 | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.71101 | 100.01 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.71101 | 103.55 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.71155 | 100.82 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-132 | FROM->TO | 338758 5HEBER.N# 161 505422 GREERSF5 161 1 | 205 | 205 | 1 | 109.15 | 505418 JONESBO5 161 774620 G23-132-TAP 161 1 | TDF Impact | Rebuild the existing 5HEBER.N# to GREERSF5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-134 | FROM->TO | 515077 FIXICO 2 69.0 997805 FIXICO4 69.0 4 | 62 | 67 | 0.20913 | 110.5 | 510902 WELETK4 138 774660 G23-134-TAP 138 1 | TDF Impact | Upgrade the existing FIXICO4 138/69 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-134 | FROM->TO | 515078 FIXICO 4 138 997805 FIXICO4 69.0 4 | 62 | 67 | 0.20913 | 109.05 | 510902 WELETK4 138 774660 G23-134-TAP 138 1 | TDF Impact | Upgrade the existing FIXICO4 138/69 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-135 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.28893 | 113.05 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-135 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.28893 | 113.05 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-135 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.28893 | 113.05 | Potential P4 Event - POI 508359_5 | TDF Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-138 | FROM->TO | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | 1182 | 1182 | 0.31274 | 109.85 | Potential P4 Event - POI 509745_2 | TDF Impact | Rebuild the existing TONECE7 to G23-138-TAP 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-138 | FROM->TO | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | 1182 | 1182 | 0.31274 | 110.93 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Rebuild the existing TONECE7 to G23-138-TAP 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-138 | FROM->TO | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | 1182 | 1182 | 0.31274 | 111.12 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | TDF Impact | Rebuild the existing TONECE7 to G23-138-TAP 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-138 | FROM->TO | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | 1182 | 1182 | 0.31274 | 111.12 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT:::: | TDF Impact | Rebuild the existing TONECE7 to G23-138-TAP 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-138 | FROM->TO | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | 1182 | 1182 | 0.31387 | 109.67 | Potential P4 Event - POI 509745_0 | TDF Impact | Rebuild the existing TONECE7 to G23-138-TAP 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-138 | FROM->TO | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | 1182 | 1182 | 0.31387 | 109.96 | Potential P4 Event - POI 509745_1 | TDF Impact | Rebuild the existing TONECE7 to G23-138-TAP 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-180 | FROM->TO | 507189 NHUNTNT5 161 775580 G23-180-TAP 161 1 | 158 | 178 | 0.58964 | 101.01 | 515261 BONANZT5 161 515299 BEVYTAP5 161 1 | TDF Impact | Rebuild the existing NHUNTNT5 to G23-180-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 514803 SOONER 7 345 515576 RANCHRD7 345 1 | 1716 | 1793 | 1 | 101.65 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 514803 SOONER 7 345 515576 RANCHRD7 345 1 | 1716 | 1793 | 1 | 101.68 | Potential P4 Event - POI 532794_5 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 514803 SOONER 7 345 515576 RANCHRD7 345 1 | 1716 | 1793 | 1 | 101.69 | Potential P4 Event - POI 532794_2 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 514803 SOONER 7 345 515576 RANCHRD7 345 1 | 1716 | 1793 | 1 | 101.73 | Potential P4 Event - POI 532794_7 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.21093 | 103.43 | P12:345:WERE:ROSE-WOLF-345:::EHV: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.21093 | 103.43 | Potential P4 Event - POI 532794_6 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.21093 | 118.12 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.2541 | 113.97 | Potential P4 Event - POI 532794_4 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35789 | 115.05 | Potential P4 Event - POI 532782_12 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.36244 | 109.83 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.36455 | 124.84 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.36455 | 124.84 | Potential P4 Event - POI 515852_9 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.36486 | 112.77 | Potential P4 Event - POI 515852_0 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.36952 | 106.96 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.36979 | 107.05 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA_1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.36979 | 107.05 | P23:345:GMO:SIBLEY-R1-3:::EHV: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.36992 | 112.24 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.36992 | 112.92 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.36992 | 112.92 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.36992 | 112.94 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.36993 | 107.11 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.36998 | 111.76 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.36998 | 112.66 | Potential P4 Event - POI 773480_0 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.36998 | 114.25 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37008 | 106.25 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37008 | 108.05 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37009 | 106.61 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.3701 | 106.36 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37012 | 106.92 | P23:345:AMMO::MONTGOMERY:V43:: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37013 | 106.2 | 659448 DAGLUM__-BE4 230 659450 BRADY___-PP4 230 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37014 | 106.35 | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37014 | 106.43 | 337376 7SAREPTA% 345 508809 LONGWD 7 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37015 | 106.26 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37015 | 106.51 | 532798 VIOLA 7 345 3WXFMR VIOLA1 _1 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37019 | 106.5 | 532663 LEC U5 24.0 532854 LEC U5 6 230 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37019 | 109.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37022 | 106.45 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37022 | 106.46 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37022 | 106.69 | P12:138:AEPW:CATOOSA4:T.S.E.-4::: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37023 | 106.24 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37023 | 106.25 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37023 | 106.64 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37023 | 107.36 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37023 | 107.81 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37023 | 110.27 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37024 | 106.95 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37024 | 107.91 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37025 | 106.56 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37025 | 109.55 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37026 | 106.47 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 106.32 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 106.34 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 106.34 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 106.34 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 106.34 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 106.34 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 106.37 | 603002 WILMART7 115 603294 MEC CT2 115 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 106.42 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 106.46 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 106.5 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 106.54 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 106.54 | 776381 GEN-2023-220 345 776382 G23-220XFMR1 34.5 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 106.54 | 776401 GEN-2023-221 345 776402 G23-221XFMR1 34.5 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 106.54 | GEN-2023-220_POI_776380_Generator_outage | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 106.54 | GEN-2023-221_POI_776400_Generator_outage | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 106.54 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 106.59 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 106.6 | GEN-2023-099_POI_532766_Generator_outage | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 106.63 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 106.75 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 106.91 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 106.97 | P23:345:XEL:8H14 PRI | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 106.98 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 106.98 | P23:345:XEL:8H17 PRI AS | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 106.99 | P11:115:XEL:HBR #6 7 8 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 107.01 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 107.04 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 107.04 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 107.06 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 107.16 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 107.22 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 107.22 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 107.23 | P23:345:XEL:8N17 SHC | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 107.23 | P23:345:XEL:8N22 SHC | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 107.3 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 107.31 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 107.31 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 107.31 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 107.59 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 107.64 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 107.68 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 107.76 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 107.77 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 107.77 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 107.87 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 108.02 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 108.05 | P23:500:EES-EAI:KEO:B4921 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 108.16 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 108.26 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 108.39 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37027 | 113.22 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37028 | 106.59 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37028 | 106.96 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37028 | 106.96 | P23:500:EES:PERRYVILLE:R9872::: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37028 | 107.01 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37028 | 108.04 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37028 | 108.35 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.3703 | 106.45 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.3703 | 107.08 | P12:500-161:EES-EAI:M:NEW_MAD:PORTGV:WMPEHV:8BHAMSTE:HATI_S:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.3703 | 107.13 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.3703 | 107.22 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.3703 | 107.22 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.3703 | 107.4 | P23:500:EAI-TVA:NBF_WEST M~1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37031 | 106.8 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37031 | 107.31 | P23:500:EES-EAI:KEO:B4931 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37034 | 106.47 | 300070 5CLARK 161 541208 NEVADA 5 161 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37034 | 106.83 | 547469 RIV4525 161 547729 BAX488 5 161 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37034 | 106.86 | 547487 HOC404 5 161 547729 BAX488 5 161 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37036 | 106.57 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37037 | 106.42 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37037 | 106.64 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37038 | 106.83 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37038 | 106.83 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW::: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37039 | 106.72 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37039 | 107.03 | P23:345:MEC:GDMEC 902 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37041 | 108.25 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37041 | 108.77 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37046 | 106.85 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37052 | 107.41 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37052 | 107.63 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37053 | 108.76 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37053 | 108.9 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37053 | 109.78 | P12:138:WERE:CRSW-OGE-138:::HV: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37053 | 110.78 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37054 | 107.53 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37062 | 108.26 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37063 | 112.07 | P23:345:WERE:WICH-345-116:::EHV: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37097 | 112.14 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37103 | 109.51 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37103 | 109.56 | 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37103 | 109.61 | 767240 G22-013-TAP 345 776600 G23-231-TAP 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37139 | 111.51 | P12:345:WERE:VIOL-WICH-345:::EHV: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37178 | 124.35 | Potential P4 Event - POI 532798_2 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37223 | 106.47 | 300138 4CLEVLND 138 512729 CLEVLND 4 138 Z1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37275 | 123.23 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37275 | 123.24 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37276 | 123.43 | Potential P4 Event - POI 532798_1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37366 | 122.65 | P42:345:OKGE:SB_REOW7319:::: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37396 | 123.62 | Potential P4 Event - POI 515543_2 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37441 | 118.78 | P42:345:OKGE:SB_REOW7312:::: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.39482 | 112.36 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB:::: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.39499 | 111.38 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7::: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.40977 | 113.17 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.40977 | 113.17 | Potential P4 Event - POI 514803_3 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.40977 | 114.54 | 512694 CLEVLND7 345 560056 G15066_T 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.41012 | 114.67 | P23:345:GRDA:CLEVLND CB13280:::EHV: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.41012 | 114.67 | P42:345:GRDA:CLEVLND CB13280:::EHV: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.47271 | 118.18 | Potential P4 Event - POI 514803_12 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-212 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.25635 | 113.05 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-212 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.25635 | 113.05 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-212 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.25635 | 113.05 | Potential P4 Event - POI 508359_5 | TDF Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27L | GEN-2023-134 | FROM->TO | 515077 FIXICO 2 69.0 997806 FIXICO4 69.0 4 | 62 | 67 | 0.20654 | 101.72 | 510902 WELETK4 138 774660 G23-134-TAP 138 1 | TDF Impact | Upgrade the existing FIXICO4 138/69 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27L | GEN-2023-134 | FROM->TO | 515078 FIXICO 4 138 997806 FIXICO4 69.0 4 | 62 | 67 | 0.20654 | 100.46 | 510902 WELETK4 138 774660 G23-134-TAP 138 1 | TDF Impact | Upgrade the existing FIXICO4 138/69 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-009 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.49353 | 105.14 | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | TDF Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-009 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.49353 | 105.14 | 521157 HUGO 7 345 3WXFMR HUGO 1 1 | TDF Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.2202 | 116.62 | P12:161:AEPW-EMDE:FLINTCR5:739952::: | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.22345 | 107.52 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.22345 | 107.55 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23684 | 107.8 | Potential P4 Event - POI 509745_2 | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23684 | 108.77 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23704 | 107.34 | Potential P4 Event - POI 509745_0 | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23704 | 107.68 | Potential P4 Event - POI 509745_1 | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23907 | 100.24 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23909 | 101.06 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23923 | 101.45 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.2396 | 112.16 | 512650 GRDA1 7 345 774740 G23-138-TAP 345 1 | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.2396 | 117.09 | Potential P4 Event - POI 774740_1 | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.2396 | 117.24 | Potential P4 Event - POI 774740_0 | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.2396 | 117.24 | Potential P4 Event - POI 774740_2 | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.2396 | 120.46 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23964 | 112.06 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23964 | 112.06 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT:::: | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23965 | 111.83 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.27994 | 104 | P13:69-138:AEPW:PRY-JCT2:::: | TDF Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.2202 | 111.68 | P12:161:AEPW-EMDE:FLINTCR5:739952::: | TDF Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.22345 | 102.63 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | TDF Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.22345 | 102.64 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | TDF Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23684 | 103.01 | Potential P4 Event - POI 509745_2 | TDF Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23684 | 103.98 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23704 | 102.56 | Potential P4 Event - POI 509745_0 | TDF Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23704 | 102.89 | Potential P4 Event - POI 509745_1 | TDF Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.2396 | 107.33 | 512650 GRDA1 7 345 774740 G23-138-TAP 345 1 | TDF Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.2396 | 112.2 | Potential P4 Event - POI 774740_1 | TDF Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.2396 | 112.33 | Potential P4 Event - POI 774740_0 | TDF Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.2396 | 112.33 | Potential P4 Event - POI 774740_2 | TDF Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.2396 | 115.5 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | TDF Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23964 | 107.14 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23964 | 107.14 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT:::: | TDF Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23965 | 106.94 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | TDF Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20242 | 101.85 | Potential P4 Event - POI 509745_2 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20242 | 102.77 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20259 | 101.36 | Potential P4 Event - POI 509745_0 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20259 | 101.74 | Potential P4 Event - POI 509745_1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.2055 | 107.33 | 512650 GRDA1 7 345 774740 G23-138-TAP 345 1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.2055 | 112.44 | Potential P4 Event - POI 774740_0 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.2055 | 112.45 | Potential P4 Event - POI 774740_2 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.2055 | 112.71 | Potential P4 Event - POI 774740_1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.2055 | 115.54 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20558 | 106.38 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20558 | 106.38 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT:::: | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20558 | 107.01 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20242 | 103.09 | Potential P4 Event - POI 509745_2 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20242 | 104.01 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20259 | 102.58 | Potential P4 Event - POI 509745_0 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20259 | 102.97 | Potential P4 Event - POI 509745_1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.2055 | 108.56 | 512650 GRDA1 7 345 774740 G23-138-TAP 345 1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.2055 | 113.64 | Potential P4 Event - POI 774740_0 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.2055 | 113.65 | Potential P4 Event - POI 774740_2 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.2055 | 113.99 | Potential P4 Event - POI 774740_1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.2055 | 116.75 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20558 | 107.21 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20558 | 107.21 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT:::: | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20558 | 108 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | 335 | 335 | 1 | 111.9 | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | TDF Impact | DRYGULCH5 to G23-028-TAP 161 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.30684 | 163.89 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.30429 | 125.42 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.34195 | 178.83 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.34195 | 183.73 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 113.31 | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | TDF Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 133.85 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | 335 | 335 | 1 | 111.9 | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | TDF Impact | DRYGULCH5 to G23-028-TAP 161 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.30684 | 163.89 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.30429 | 125.42 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.21069 | 167.27 | 512654 PENSA 5 161 3WXFMR PENAUTO1 1 | TDF Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.34195 | 178.83 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.21069 | 172.12 | 512654 PENSA 5 161 3WXFMR PENAUTO1 1 | TDF Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.34195 | 183.73 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 113.31 | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | TDF Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 133.85 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-075 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.59873 | 100.89 | Potential P4 Event - POI 532794_2 | TDF Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-075 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.60288 | 100.68 | Potential P4 Event - POI 532794_5 | TDF Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-075 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.60306 | 100.54 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-075 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.60306 | 100.54 | Potential P4 Event - POI 532794_9 | TDF Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-076 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.59873 | 100.89 | Potential P4 Event - POI 532794_2 | TDF Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-076 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.60288 | 100.68 | Potential P4 Event - POI 532794_5 | TDF Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-076 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.60306 | 100.54 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-076 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.60306 | 100.54 | Potential P4 Event - POI 532794_9 | TDF Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-092 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.42371 | 105.14 | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | TDF Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-092 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.42371 | 105.14 | 521157 HUGO 7 345 3WXFMR HUGO 1 1 | TDF Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 435 | 435 | 1 | 108.78 | 523777 WHEELER 6 230 774000 G23-101-TAP 230 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-101 | FROM->TO | 523777 WHEELER 6 230 774000 G23-101-TAP 230 1 | 353 | 353 | 0.33028 | 102.2 | P12:345:OKGE-AEP:BKRBKR4291:::: | TDF Impact | Rebuild the existing WHEELER 6 to G23-101-TAP 230 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-101 | FROM->TO | 523777 WHEELER 6 230 774000 G23-101-TAP 230 1 | 353 | 353 | 1 | 135.11 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing WHEELER 6 to G23-101-TAP 230 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.68783 | 142.32 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.68783 | 142.32 | Potential P4 Event - POI 515375_23 | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.68783 | 142.32 | Potential P4 Event - POI 515852_0 | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.69387 | 100.32 | GEN-2023-102_POI_515852_Generator_outage | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.70679 | 111 | Potential P4 Event - POI 515852_4 | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.70679 | 111 | Potential P4 Event - POI 515852_8 | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.70688 | 104.64 | Potential P4 Event - POI 515375_27 | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.70688 | 104.64 | Potential P4 Event - POI 515375_36 | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.70952 | 109.17 | P42:345:OKGE:SB_REOW7312:::: | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.70952 | 109.17 | Potential P4 Event - POI 515543_0 | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.70964 | 108.43 | P12:345:OKGE:BKRBKR421:::: | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.70964 | 109.31 | Potential P4 Event - POI 515543_1 | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.70976 | 107.63 | P12:345:OKGE:BKRBKR400:::: | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.71006 | 108.25 | Potential P4 Event - POI 514715_2 | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.71102 | 101.58 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.71102 | 104.82 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.71107 | 100.32 | 515852 DGRASSE7 345 776821 GEN-2023-102 345 1 | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.71117 | 100.5 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.7113 | 100.88 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.71137 | 101.67 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.71139 | 101.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.71141 | 100.57 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.71158 | 102.96 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.71474 | 100.49 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.71474 | 100.81 | P12:138:WFEC:MOORELND_CLEOCRNR:::: | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.71474 | 100.85 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.71604 | 100.53 | 521065 TALOGA 4 138 765215 G20-010-TAP 138 1 | TDF Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-132 | FROM->TO | 338758 5HEBER.N# 161 505422 GREERSF5 161 1 | 205 | 205 | 1 | 111.47 | 505418 JONESBO5 161 774620 G23-132-TAP 161 1 | TDF Impact | Rebuild the existing 5HEBER.N# to GREERSF5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-134 | FROM->TO | 515077 FIXICO 2 69.0 997806 FIXICO4 69.0 4 | 62 | 67 | 0.20772 | 107.03 | 510902 WELETK4 138 774660 G23-134-TAP 138 1 | TDF Impact | Upgrade the existing FIXICO4 138/69 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-134 | FROM->TO | 515078 FIXICO 4 138 997806 FIXICO4 69.0 4 | 62 | 67 | 0.20772 | 106.29 | 510902 WELETK4 138 774660 G23-134-TAP 138 1 | TDF Impact | Upgrade the existing FIXICO4 138/69 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-135 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.28908 | 109.58 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-135 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.28908 | 109.58 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-135 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.28908 | 109.58 | Potential P4 Event - POI 508359_5 | TDF Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-138 | FROM->TO | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | 1182 | 1182 | 0.3117 | 106.73 | Potential P4 Event - POI 509745_2 | TDF Impact | Rebuild the existing TONECE7 to G23-138-TAP 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-138 | FROM->TO | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | 1182 | 1182 | 0.3117 | 107.7 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Rebuild the existing TONECE7 to G23-138-TAP 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-138 | FROM->TO | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | 1182 | 1182 | 0.3117 | 107.79 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | TDF Impact | Rebuild the existing TONECE7 to G23-138-TAP 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-138 | FROM->TO | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | 1182 | 1182 | 0.3117 | 107.79 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT:::: | TDF Impact | Rebuild the existing TONECE7 to G23-138-TAP 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-138 | FROM->TO | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | 1182 | 1182 | 0.31267 | 106.53 | Potential P4 Event - POI 509745_0 | TDF Impact | Rebuild the existing TONECE7 to G23-138-TAP 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-138 | FROM->TO | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | 1182 | 1182 | 0.31267 | 106.8 | Potential P4 Event - POI 509745_1 | TDF Impact | Rebuild the existing TONECE7 to G23-138-TAP 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-180 | FROM->TO | 507189 NHUNTNT5 161 775580 G23-180-TAP 161 1 | 158 | 178 | 0.59014 | 101.74 | 515261 BONANZT5 161 515299 BEVYTAP5 161 1 | TDF Impact | Rebuild the existing NHUNTNT5 to G23-180-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 514803 SOONER 7 345 515576 RANCHRD7 345 1 | 1716 | 1793 | 1 | 101.3 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 514803 SOONER 7 345 515576 RANCHRD7 345 1 | 1716 | 1793 | 1 | 101.31 | Potential P4 Event - POI 532794_2 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 514803 SOONER 7 345 515576 RANCHRD7 345 1 | 1716 | 1793 | 1 | 101.32 | Potential P4 Event - POI 532794_5 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 514803 SOONER 7 345 515576 RANCHRD7 345 1 | 1716 | 1793 | 1 | 101.33 | Potential P4 Event - POI 532794_7 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.20664 | 106.29 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.24546 | 107.66 | Potential P4 Event - POI 532794_4 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.34551 | 110.16 | Potential P4 Event - POI 532782_12 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.34829 | 104.29 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35208 | 118.9 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35208 | 118.9 | Potential P4 Event - POI 515852_9 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35236 | 108.16 | Potential P4 Event - POI 515375_23 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.3542 | 104.07 | P23:345:WERE:BUFF-345-543:::EHV: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35667 | 102.82 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35708 | 102.84 | P12:345:AMMO-GMO::OVERTON:SIBLEY:3 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35713 | 102.48 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35716 | 102.13 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35716 | 102.24 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35717 | 104.24 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.3572 | 102.25 | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35721 | 102.29 | 532798 VIOLA 7 345 3WXFMR VIOLA1 _1 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35722 | 102.15 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35722 | 102.45 | 532663 LEC U5 24.0 532854 LEC U5 6 230 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35722 | 102.72 | P23:345:AMMO::MONTGOMERY:V43:: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35725 | 102.38 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35725 | 102.38 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35727 | 105.47 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35728 | 102.2 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35728 | 102.21 | 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35728 | 102.21 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35728 | 102.34 | 300040 7FLETCH 345 300472 7SALEMTP 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35728 | 102.52 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35728 | 103.99 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35729 | 105.72 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.3573 | 102.44 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.3573 | 103.45 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.3573 | 103.51 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35731 | 102.79 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35731 | 102.79 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35732 | 102.34 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35732 | 102.37 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35732 | 103.11 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 102.14 | 659336 TANDE___-BE3 345 659479 TRADEWND-UA3 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 102.15 | 631243 J455 POI2 345 635420 CLAY CO 3 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 102.21 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 102.21 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 102.21 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 102.24 | 603002 WILMART7 115 603294 MEC CT2 115 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 102.26 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 102.26 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 102.26 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 102.27 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 102.36 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 102.38 | 620482 J510 ASTOR 3 345 620483 ASTORIA 3 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 102.38 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 102.38 | 776381 GEN-2023-220 345 776382 G23-220XFMR1 34.5 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 102.38 | 776401 GEN-2023-221 345 776402 G23-221XFMR1 34.5 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 102.38 | GEN-2023-220_POI_776380_Generator_outage | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 102.38 | GEN-2023-221_POI_776400_Generator_outage | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 102.4 | GEN-2023-099_POI_532766_Generator_outage | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 102.42 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 102.43 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 102.5 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 102.76 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 102.83 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 102.85 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 102.86 | P11:115:XEL:HBR #6 7 8 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 102.88 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 102.88 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 102.88 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 102.9 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 102.95 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 103 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 103.05 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 103.05 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 103.05 | P23:345:XEL:8N8 MNN | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 103.06 | P23:345:XEL:8N17 SHC | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 103.06 | P23:345:XEL:8N22 SHC | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 103.12 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 103.13 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 103.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 103.32 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 103.36 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 103.39 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 103.44 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 103.44 | P23:345:MEC:CBEC 908 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 103.46 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 103.51 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 103.61 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 103.63 | P23:345:MEC:CBEC 905 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 103.84 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 104.02 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 104.07 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35734 | 107.86 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35735 | 102.48 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35735 | 102.85 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35735 | 102.85 | P23:500:EES:PERRYVILLE:R9872::: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35735 | 103.79 | P23:500:EES-EAI:KEO:B4921 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35736 | 102.32 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35736 | 104.2 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35738 | 102.61 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35738 | 102.98 | P12:500-161:EES-EAI:M:NEW_MAD:PORTGV:WMPEHV:8BHAMSTE:HATI_S:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35738 | 103.02 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35738 | 103.07 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35738 | 103.1 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35738 | 103.24 | P23:500:EAI-TVA:NBF_WEST M~1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35739 | 103.17 | P23:500:EES-EAI:KEO:B4931 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35741 | 102.26 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35742 | 102.81 | P12:345:AEPW:WEKIWA-7:T.NO.-7::: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35742 | 107.46 | P23:345:WERE:WICH-345-116:::EHV: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35744 | 102.48 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35745 | 102.56 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35745 | 102.66 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35745 | 102.66 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW::: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35745 | 102.9 | P23:345:MEC:GDMEC 902 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35746 | 102.49 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35747 | 104.07 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35747 | 104.66 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35747 | 106.09 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.3575 | 102.76 | 547469 RIV4525 161 547729 BAX488 5 161 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.3575 | 102.81 | 547487 HOC404 5 161 547729 BAX488 5 161 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35751 | 104.37 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35751 | 104.5 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35752 | 103.26 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35753 | 103.43 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35754 | 102.62 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35761 | 106.27 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35764 | 103.2 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35786 | 104.23 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35804 | 107.85 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35804 | 107.86 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35804 | 108.83 | Potential P4 Event - POI 773480_1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35804 | 108.84 | Potential P4 Event - POI 773480_0 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35804 | 110.54 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35806 | 105.1 | P12:138:OKGE-WFEC-OMPA-WERE:BKRBKR71:::: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35806 | 108.26 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35806 | 109.06 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35809 | 117.9 | Potential P4 Event - POI 532798_2 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35811 | 109.11 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35811 | 109.11 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35813 | 105.99 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35816 | 106.83 | P12:345:WERE:VIOL-WICH-345:::EHV: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35817 | 104.09 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35817 | 104.23 | 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35817 | 104.26 | 767240 G22-013-TAP 345 776600 G23-231-TAP 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35903 | 117.03 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35903 | 117.11 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35903 | 117.14 | Potential P4 Event - POI 763421_0 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.35978 | 116.48 | P42:345:OKGE:SB_REOW7319:::: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.36002 | 117.33 | Potential P4 Event - POI 515543_2 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.36046 | 113.27 | P42:345:OKGE:SB_REOW7312:::: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.36189 | 112.16 | P12:345:OKGE:BKRBKR400:::: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.36868 | 104.86 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7::: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37194 | 107.87 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB:::: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37338 | 104.32 | P12:345:OKGE:BKRBKR43_4:27S_32S::: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.37532 | 105.5 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1532 | 1793 | 0.41361 | 111.95 | Potential P4 Event - POI 514803_3 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-212 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.25637 | 109.58 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-212 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.25637 | 109.58 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-212 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.25637 | 109.58 | Potential P4 Event - POI 508359_5 | TDF Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-009 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.30499 | 102.7 | P23:345:AEPW:VALLIANT CB 3413A NBTB:::: | TDF Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-009 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.30499 | 102.7 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT:::: | TDF Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-009 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.30735 | 105.06 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-009 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.49363 | 110.16 | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | TDF Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-009 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.49363 | 110.16 | 521157 HUGO 7 345 3WXFMR HUGO 1 1 | TDF Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20285 | 100.83 | Potential P4 Event - POI 509745_2 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20285 | 101.05 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20299 | 100.63 | Potential P4 Event - POI 509745_0 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20299 | 100.73 | Potential P4 Event - POI 509745_1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20583 | 108.85 | 512650 GRDA1 7 345 774740 G23-138-TAP 345 1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20583 | 114.3 | Potential P4 Event - POI 774740_0 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20583 | 114.3 | Potential P4 Event - POI 774740_2 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20583 | 114.46 | Potential P4 Event - POI 774740_1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20583 | 117.52 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20592 | 108.01 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20592 | 108.01 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT:::: | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20592 | 108.43 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20285 | 101.89 | Potential P4 Event - POI 509745_2 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20285 | 102.11 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20299 | 101.7 | Potential P4 Event - POI 509745_0 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20299 | 101.79 | Potential P4 Event - POI 509745_1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20583 | 110.11 | 512650 GRDA1 7 345 774740 G23-138-TAP 345 1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20583 | 115.72 | Potential P4 Event - POI 774740_0 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20583 | 115.72 | Potential P4 Event - POI 774740_2 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20583 | 115.91 | Potential P4 Event - POI 774740_1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20583 | 119 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20592 | 109.02 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20592 | 109.02 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT:::: | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20592 | 109.51 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | TDF Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | 335 | 335 | 1 | 111.67 | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | TDF Impact | DRYGULCH5 to G23-028-TAP 161 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.30765 | 141.88 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.30516 | 127.14 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.34275 | 155.24 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.34275 | 145.23 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 0.36113 | 100.36 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | TDF Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 113.23 | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | TDF Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 133.78 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | 335 | 335 | 1 | 111.67 | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | TDF Impact | DRYGULCH5 to G23-028-TAP 161 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.30765 | 141.88 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.30516 | 127.14 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.21149 | 146.05 | 512654 PENSA 5 161 3WXFMR PENAUTO1 1 | TDF Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.34275 | 155.24 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.21149 | 136.91 | 512654 PENSA 5 161 3WXFMR PENAUTO1 1 | TDF Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.34275 | 145.23 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 0.47548 | 100.36 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | TDF Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 113.23 | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | TDF Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 133.78 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | TDF Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-056 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.70399 | 102.3 | P42:345:OKGE:SB_FTTH7386:::: | TDF Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-056 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.70605 | 102.35 | P12:345:OKGE:BKRBKR295:::: | TDF Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-056 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.70605 | 102.35 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1 | TDF Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-056 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.70605 | 102.35 | P41:345:OKGE:SB_MUGE7385:::: | TDF Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-056 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.7541 | 110.08 | 515264 TARBY 5 161 515265 SHAD-PT5 161 1 | TDF Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-056 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.7541 | 112.62 | 515254 SUNSTCN5 161 515265 SHAD-PT5 161 1 | TDF Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-056 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.7541 | 112.88 | P12:161:OKGE-SWPA-WFEC:BKRBKR4:::: | TDF Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-056 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.7541 | 113.4 | 505582 RS KERR5 161 515254 SUNSTCN5 161 1 | TDF Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.58964 | 109.07 | 509050 KEATCHI4 138 509064 GEORPAC4 138 1 | TDF Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.58964 | 110.24 | 509050 KEATCHI4 138 509052 STONWAL4 138 1 | TDF Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.58964 | 111.31 | 507793 LEASIDE 4 138 509052 STONWAL4 138 1 | TDF Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.6004 | 113.43 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.6004 | 113.43 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.6004 | 113.43 | Potential P4 Event - POI 508359_5 | TDF Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.60233 | 104.88 | Potential P4 Event - POI 508563_3 | TDF Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.60235 | 104.87 | P42:345:AEPW:PIRKEY CB 13430 NBTB+FAULT:::: | TDF Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.60235 | 104.87 | Potential P4 Event - POI 508563_1 | TDF Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.60238 | 104.87 | P12:345:AEPW:PIRKEY7:DIANA7::: | TDF Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.61206 | 102.53 | P23:500:AEPW-EES:ABF_HTBG-A | TDF Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.61681 | 105.32 | P13:345,230:CLEC::DOLHILL::1 | TDF Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.61681 | 105.32 | P13:345-230:CLEC::DOLHILL7:1 | TDF Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.61681 | 105.32 | P13:345-230:CLEC:DOLET:5092 | TDF Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-064 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.2858 | 102.3 | P42:345:OKGE:SB_FTTH7386:::: | TDF Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-064 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.28763 | 102.35 | P12:345:OKGE:BKRBKR295:::: | TDF Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-064 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.28763 | 102.35 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1 | TDF Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-064 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.28763 | 102.35 | P41:345:OKGE:SB_MUGE7385:::: | TDF Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-064 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.51794 | 110.08 | 515264 TARBY 5 161 515265 SHAD-PT5 161 1 | TDF Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-064 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.51794 | 112.62 | 515254 SUNSTCN5 161 515265 SHAD-PT5 161 1 | TDF Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-064 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.51794 | 112.88 | P12:161:OKGE-SWPA-WFEC:BKRBKR4:::: | TDF Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-064 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.51794 | 113.4 | 505582 RS KERR5 161 515254 SUNSTCN5 161 1 | TDF Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-092 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.26585 | 102.7 | P23:345:AEPW:VALLIANT CB 3413A NBTB:::: | TDF Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-092 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.26585 | 102.7 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT:::: | TDF Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-092 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.2681 | 105.06 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-092 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.42381 | 110.16 | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | TDF Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-092 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.42381 | 110.16 | 521157 HUGO 7 345 3WXFMR HUGO 1 1 | TDF Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 435 | 435 | 1 | 108.88 | 523777 WHEELER 6 230 774000 G23-101-TAP 230 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-101 | FROM->TO | 523777 WHEELER 6 230 774000 G23-101-TAP 230 1 | 439 | 439 | 1 | 108.32 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing WHEELER 6 to G23-101-TAP 230 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-135 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.30537 | 100.46 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-135 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.30537 | 100.46 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-135 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.30537 | 100.46 | Potential P4 Event - POI 508359_5 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-135 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.28415 | 112.2 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-135 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.28415 | 112.2 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-135 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.28415 | 112.2 | Potential P4 Event - POI 508359_5 | TDF Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-138 | FROM->TO | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | 1195 | 1195 | 0.31531 | 100.76 | Potential P4 Event - POI 509745_2 | TDF Impact | Rebuild the existing TONECE7 to G23-138-TAP 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-138 | FROM->TO | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | 1195 | 1195 | 0.31531 | 100.97 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Rebuild the existing TONECE7 to G23-138-TAP 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-138 | FROM->TO | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | 1195 | 1195 | 0.31531 | 101.03 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | TDF Impact | Rebuild the existing TONECE7 to G23-138-TAP 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-138 | FROM->TO | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | 1195 | 1195 | 0.31531 | 101.03 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT:::: | TDF Impact | Rebuild the existing TONECE7 to G23-138-TAP 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-138 | FROM->TO | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | 1195 | 1195 | 0.31614 | 100.63 | Potential P4 Event - POI 509745_0 | TDF Impact | Rebuild the existing TONECE7 to G23-138-TAP 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-138 | FROM->TO | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | 1195 | 1195 | 0.31614 | 100.69 | Potential P4 Event - POI 509745_1 | TDF Impact | Rebuild the existing TONECE7 to G23-138-TAP 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-211 | FROM->TO | 514803 SOONER 7 345 515576 RANCHRD7 345 1 | 1716 | 1793 | 1 | 100.82 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-211 | FROM->TO | 514803 SOONER 7 345 515576 RANCHRD7 345 1 | 1716 | 1793 | 1 | 100.83 | Potential P4 Event - POI 532794_5 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-211 | FROM->TO | 514803 SOONER 7 345 515576 RANCHRD7 345 1 | 1716 | 1793 | 1 | 100.83 | Potential P4 Event - POI 532794_7 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-211 | FROM->TO | 514803 SOONER 7 345 515576 RANCHRD7 345 1 | 1716 | 1793 | 1 | 100.84 | Potential P4 Event - POI 532794_2 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-211 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.24919 | 100.07 | Potential P4 Event - POI 532794_4 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1793 | 1793 | 0.3574 | 102.5 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1793 | 1793 | 0.3574 | 102.5 | Potential P4 Event - POI 515852_9 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1793 | 1793 | 0.36341 | 102.63 | Potential P4 Event - POI 532798_2 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1793 | 1793 | 0.36473 | 101.81 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1793 | 1793 | 0.36473 | 101.82 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1793 | 1793 | 0.36473 | 101.85 | Potential P4 Event - POI 532798_1 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1793 | 1793 | 0.3655 | 102.19 | Potential P4 Event - POI 515543_2 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1793 | 1793 | 1 | 101.81 | P42:345:OKGE:SB_RARD7383:::: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1793 | 1793 | 1 | 102.64 | P12:345:OKGE:BKRBKR357_1:::: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1793 | 1793 | 1 | 102.64 | P42:345:OKGE:SB_SOER7383:::: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1793 | 1793 | 1 | 102.64 | Potential P4 Event - POI 514803_8 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1793 | 1793 | 1 | 102.67 | Potential P4 Event - POI 514803_0 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1793 | 1793 | 1 | 102.68 | Potential P4 Event - POI 514803_7 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-212 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.24242 | 100.46 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-212 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.24242 | 100.46 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-212 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.24242 | 100.46 | Potential P4 Event - POI 508359_5 | TDF Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-212 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.2515 | 112.2 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-212 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.2515 | 112.2 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-212 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.2515 | 112.2 | Potential P4 Event - POI 508359_5 | TDF Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-009 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.17163 | 113.05 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-009 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.17163 | 113.05 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-009 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.17163 | 113.05 | Potential P4 Event - POI 508359_5 | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-009 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.30474 | 101.11 | P23:345:AEPW:VALLIANT CB 3413A NBTB:::: | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-009 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.30474 | 101.11 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT:::: | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-009 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.30696 | 102.47 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-009 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.49466 | 103.89 | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-009 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.49466 | 103.89 | 521157 HUGO 7 345 3WXFMR HUGO 1 1 | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.22032 | 117.54 | P12:161:AEPW-EMDE:FLINTCR5:739952::: | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.22359 | 108.4 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.22359 | 108.42 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23693 | 109.04 | Potential P4 Event - POI 509745_2 | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23693 | 110.11 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23716 | 108.59 | Potential P4 Event - POI 509745_0 | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23716 | 108.96 | Potential P4 Event - POI 509745_1 | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23922 | 101.29 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23934 | 101.17 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.2394 | 100.18 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.2394 | 103.05 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23941 | 101.53 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23984 | 114.03 | 512650 GRDA1 7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23984 | 119.2 | Potential P4 Event - POI 774740_1 | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23984 | 119.3 | Potential P4 Event - POI 774740_2 | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23984 | 119.32 | Potential P4 Event - POI 774740_0 | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23984 | 122.63 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23985 | 113.61 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23985 | 113.83 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23985 | 113.83 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.24021 | 100.5 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.22032 | 112.52 | P12:161:AEPW-EMDE:FLINTCR5:739952::: | Cumulative Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.22359 | 103.42 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.22359 | 103.44 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23693 | 104.18 | Potential P4 Event - POI 509745_2 | Cumulative Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23693 | 105.24 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23716 | 103.73 | Potential P4 Event - POI 509745_0 | Cumulative Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23716 | 104.1 | Potential P4 Event - POI 509745_1 | Cumulative Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23984 | 109.1 | 512650 GRDA1 7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23984 | 114.19 | Potential P4 Event - POI 774740_1 | Cumulative Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23984 | 114.27 | Potential P4 Event - POI 774740_2 | Cumulative Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23984 | 114.29 | Potential P4 Event - POI 774740_0 | Cumulative Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23984 | 117.57 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23985 | 108.6 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23985 | 108.8 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | Cumulative Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23985 | 108.8 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997940 GROVE 138 1 | 112 | 112 | 0.18021 | 116.53 | P12:161:AEPW-EMDE:FLINTCR5:739952::: | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997940 GROVE 138 1 | 112 | 112 | 0.18447 | 103.18 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997940 GROVE 138 1 | 112 | 112 | 0.18447 | 103.22 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997940 GROVE 138 1 | 112 | 112 | 0.20249 | 102.59 | Potential P4 Event - POI 509745_2 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997940 GROVE 138 1 | 112 | 112 | 0.20249 | 103.63 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997940 GROVE 138 1 | 112 | 112 | 0.20268 | 102.14 | Potential P4 Event - POI 509745_0 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997940 GROVE 138 1 | 112 | 112 | 0.20268 | 102.5 | Potential P4 Event - POI 509745_1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997940 GROVE 138 1 | 112 | 112 | 0.20572 | 108.49 | 512650 GRDA1 7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997940 GROVE 138 1 | 112 | 112 | 0.20572 | 113.59 | Potential P4 Event - POI 774740_0 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997940 GROVE 138 1 | 112 | 112 | 0.20572 | 113.59 | Potential P4 Event - POI 774740_2 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997940 GROVE 138 1 | 112 | 112 | 0.20572 | 113.73 | Potential P4 Event - POI 774740_1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997940 GROVE 138 1 | 112 | 112 | 0.20572 | 117.08 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997940 GROVE 138 1 | 112 | 112 | 0.20577 | 107.19 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997940 GROVE 138 1 | 112 | 112 | 0.20577 | 107.19 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997940 GROVE 138 1 | 112 | 112 | 0.20577 | 107.65 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997940 GROVE 138 1 | 112 | 112 | 0.18021 | 117.47 | P12:161:AEPW-EMDE:FLINTCR5:739952::: | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997940 GROVE 138 1 | 112 | 112 | 0.18447 | 103.76 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997940 GROVE 138 1 | 112 | 112 | 0.18447 | 103.81 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997940 GROVE 138 1 | 112 | 112 | 0.20249 | 103.83 | Potential P4 Event - POI 509745_2 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997940 GROVE 138 1 | 112 | 112 | 0.20249 | 104.88 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997940 GROVE 138 1 | 112 | 112 | 0.20268 | 103.36 | Potential P4 Event - POI 509745_0 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997940 GROVE 138 1 | 112 | 112 | 0.20268 | 103.73 | Potential P4 Event - POI 509745_1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997940 GROVE 138 1 | 112 | 112 | 0.20572 | 109.68 | 512650 GRDA1 7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997940 GROVE 138 1 | 112 | 112 | 0.20572 | 114.69 | Potential P4 Event - POI 774740_0 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997940 GROVE 138 1 | 112 | 112 | 0.20572 | 114.69 | Potential P4 Event - POI 774740_2 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997940 GROVE 138 1 | 112 | 112 | 0.20572 | 114.89 | Potential P4 Event - POI 774740_1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997940 GROVE 138 1 | 112 | 112 | 0.20572 | 118.27 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997940 GROVE 138 1 | 112 | 112 | 0.20577 | 107.94 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997940 GROVE 138 1 | 112 | 112 | 0.20577 | 107.94 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997940 GROVE 138 1 | 112 | 112 | 0.20577 | 108.51 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.05039 | 103.43 | P12:345:WERE:ROSE-WOLF-345:::EHV: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.05039 | 103.43 | Potential P4 Event - POI 532794_6 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.05039 | 118.12 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.05714 | 103.77 | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | 1015 | 1015 | 0.09527 | 101.92 | Potential P4 Event - POI 532794_7 | Cumulative Impact | Line - Wolf Creek - Blackberry 345 kV
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-027 | FROM->TO | 767240 G22-013-TAP 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09527 | 102.19 | Potential P4 Event - POI 532794_7 | Cumulative Impact | Line - Wolf Creek - Blackberry 345 kV
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | 335 | 335 | 1 | 111.98 | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | Cumulative Impact | DRYGULCH5 to G23-028-TAP 161 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13235 | 151.73 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13235 | 151.8 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13322 | 150.39 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13322 | 151.53 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13446 | 146.55 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13451 | 146.2 | 547498 STL439 5 161 547657 S3G439 1 18.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13466 | 145.49 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13466 | 145.59 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13472 | 154.37 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13475 | 148.09 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13476 | 147.9 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13479 | 144.41 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13479 | 147.17 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13479 | 147.18 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13481 | 144.99 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13484 | 146.12 | P23:345:WERE:WICH-345-116:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13484 | 156.95 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13485 | 144.8 | P12:EHV:EES::7STFRAN!:7GOBKNOB%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13486 | 143.49 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13486 | 143.66 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13487 | 143.52 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13487 | 143.78 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13487 | 143.99 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13487 | 145.77 | 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13487 | 145.86 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13487 | 146.26 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13487 | 146.65 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13487 | 148.02 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13487 | 149.24 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13487 | 149.24 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13488 | 143.44 | 659348 LC_CT1-3-BE7 115 659349 LC_SWY.N-BE7 115 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13488 | 143.65 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13488 | 143.75 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13488 | 143.75 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13488 | 143.99 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13488 | 144.68 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13488 | 144.68 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 143.57 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 143.57 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 143.57 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 143.91 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 143.96 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 144.05 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 144.06 | 772981 GEN-2023-050 345 772982 G23-050XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 144.06 | 772981 GEN-2023-050 345 772985 G23-050XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 144.08 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 144.13 | GEN-2023-075_POI_773480_Generator_outage | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 144.31 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 144.36 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 144.39 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 144.51 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 144.51 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 144.56 | P23:345:XEL:8H14 PRI | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 144.57 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 144.57 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 144.74 | P23:345:MEC:LOUISA 954 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 144.88 | GEN-2023-050_POI_532793_Generator_outage | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 144.91 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 144.92 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 144.92 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 144.93 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 145.03 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 145.06 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 145.08 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 145.17 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 145.22 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 145.22 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 145.26 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 145.27 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 145.38 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 145.5 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 145.5 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 145.51 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 145.56 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 145.63 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 145.7 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 145.81 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 145.82 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 145.84 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 146.01 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 146.05 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 146.13 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 146.21 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 146.33 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 146.7 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 146.89 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 146.96 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 146.96 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 147.23 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 147.37 | 764300 GEN-2020-079 161 764310 G20-079-TAP 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 147.37 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 147.37 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 147.5 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 149.17 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13489 | 150.88 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1349 | 143.78 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1349 | 143.93 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1349 | 144.03 | P23:345:AMMO::MONTGOMERY:V43:: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13491 | 144.32 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13491 | 144.36 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13491 | 144.42 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13491 | 144.45 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13491 | 145.56 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13492 | 145.76 | P12:500-161:EES-EAI:M:NEW_MAD:PORTGV:WMPEHV:8BHAMSTE:HATI_S:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13492 | 145.77 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13492 | 145.86 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13492 | 146.35 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13492 | 148.45 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13492 | 149.28 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13493 | 146.37 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13498 | 152.71 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13498 | 153.43 | P42:345:OKGE:SB_OPKY7319:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13498 | 153.44 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13498 | 156.08 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13498 | 158.01 | Potential P4 Event - POI 560053_1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13498 | 158.04 | Potential P4 Event - POI 560053_2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13498 | 158.1 | Potential P4 Event - POI 560053_0 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13498 | 163.23 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13499 | 144.73 | 506952 CENTRTN5 161 506980 SHIPERD5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13507 | 145.6 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13513 | 164.1 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13513 | 166.41 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1352 | 166.4 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1352 | 166.4 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13524 | 149.56 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13527 | 161.5 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13527 | 165.61 | Potential P4 Event - POI 773480_2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13527 | 165.67 | Potential P4 Event - POI 773480_1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13527 | 165.72 | Potential P4 Event - POI 773480_0 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13527 | 169.52 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13527 | 169.52 | Potential P4 Event - POI 532793_16 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13527 | 169.54 | Potential P4 Event - POI 532793_13 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13527 | 171.81 | Potential P4 Event - POI 532793_18 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13531 | 150.76 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13539 | 144.99 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13555 | 146.51 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13555 | 147.65 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13555 | 149.5 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13578 | 146.45 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1359 | 152.05 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13698 | 145.88 | 547579 COM381T2 69.0 547583 FRL363 2 69.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13727 | 157.58 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13793 | 153.38 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13796 | 161.04 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13832 | 148.76 | P21:161:GRDA:SILSPWW-KANSATP5:::HV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13883 | 167.24 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.14195 | 167.59 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.14284 | 150.4 | 512632 AFTON 5 161 3WXFMR AFTAUTO1 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1465 | 150.46 | 512654 PENSA 5 161 3WXFMR PENAUTO1 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.30695 | 165.54 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13129 | 111.18 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13274 | 115.99 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13274 | 116.02 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13447 | 111.68 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13447 | 112.74 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13532 | 109.69 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13538 | 109.39 | 547498 STL439 5 161 547657 S3G439 1 18.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13562 | 108.06 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13562 | 108.12 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13562 | 117.33 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13566 | 110.85 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13569 | 107.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13571 | 109.38 | 512631 MIAMI 5 161 3WXFMR MIAAUTO2 2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13573 | 108 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13573 | 109.28 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13573 | 109.28 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13574 | 125.71 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13576 | 109.33 | P23:345:WERE:WICH-345-116:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13578 | 106.67 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13578 | 106.84 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13578 | 107.7 | P12:EHV:EES::7STFRAN!:7GOBKNOB%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13579 | 106.7 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13579 | 107.02 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13579 | 108.52 | 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13579 | 109.39 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13579 | 110.04 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13579 | 110.83 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13579 | 112.86 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13579 | 112.86 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1358 | 106.62 | 659348 LC_CT1-3-BE7 115 659349 LC_SWY.N-BE7 115 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1358 | 106.83 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1358 | 107 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1358 | 107 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1358 | 107.14 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1358 | 107.16 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1358 | 107.88 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1358 | 107.88 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1358 | 108.77 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 106.74 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 106.77 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 106.77 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 107.11 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 107.15 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 107.22 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 107.28 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 107.36 | 772981 GEN-2023-050 345 772982 G23-050XFMR1 34.5 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 107.36 | 772981 GEN-2023-050 345 772985 G23-050XFMR2 34.5 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 107.5 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 107.6 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 107.61 | GEN-2023-075_POI_773480_Generator_outage | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 107.75 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 107.75 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 107.78 | P23:345:XEL:8H14 PRI | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 107.8 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 107.8 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 107.83 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 107.89 | P23:345:MEC:LOUISA 964 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 108.1 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 108.1 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 108.11 | P23:345:XEL:8N17 SHC | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 108.12 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 108.19 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 108.21 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 108.22 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 108.3 | GEN-2023-050_POI_532793_Generator_outage | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 108.3 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 108.49 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 108.6 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 108.65 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 108.68 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 108.73 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 108.73 | P23:345:MEC:CBEC 908 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 108.86 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 108.88 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 109.03 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 109.05 | P23:345:MEC:CBEC 905 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 109.27 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 109.29 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 109.43 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 109.43 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 109.54 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 109.96 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 110.79 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 110.91 | 764300 GEN-2020-079 161 764310 G20-079-TAP 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 110.91 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13581 | 110.91 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13582 | 107.51 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13582 | 108.28 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13582 | 108.28 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13582 | 108.79 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13582 | 108.83 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13582 | 109.62 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13582 | 110.48 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13582 | 112.8 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13582 | 113.99 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13583 | 107.21 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13583 | 107.49 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13583 | 108.29 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13584 | 107.06 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13584 | 107.41 | P23:345:AMMO::MONTGOMERY:V43:: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13584 | 107.58 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13584 | 107.61 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13584 | 107.67 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13584 | 108.74 | P12:500-161:EES-EAI:M:NEW_MAD:PORTGV:WMPEHV:8BHAMSTE:HATI_S:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13584 | 108.76 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13584 | 108.85 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13584 | 111.09 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13585 | 109.31 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13585 | 111.84 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13586 | 109.31 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13592 | 116.1 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13592 | 117.07 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13592 | 117.1 | P42:345:OKGE:SB_OPKY7388:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13592 | 119.43 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13592 | 121.8 | Potential P4 Event - POI 560053_1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13592 | 121.83 | Potential P4 Event - POI 560053_2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13592 | 121.88 | Potential P4 Event - POI 560053_0 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13592 | 126.78 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13597 | 108.25 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13605 | 107.55 | 505486 NEO SPA5 161 505488 CARTHAG5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1361 | 128.8 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1361 | 131.04 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13618 | 131.01 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13618 | 131.01 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13626 | 125.84 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13626 | 130.38 | Potential P4 Event - POI 773480_2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13626 | 130.41 | Potential P4 Event - POI 773480_1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13626 | 130.46 | Potential P4 Event - POI 773480_0 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13626 | 133.88 | Potential P4 Event - POI 532793_13 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13626 | 133.89 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13626 | 133.89 | Potential P4 Event - POI 532793_16 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13626 | 136.36 | Potential P4 Event - POI 532793_18 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13632 | 114.57 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13633 | 108.08 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13639 | 109.07 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13639 | 110.22 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13639 | 111.24 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13673 | 113.66 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13792 | 112.94 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1384 | 120.06 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13872 | 121.48 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13893 | 116.01 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13925 | 109.26 | 512632 AFTON 5 161 3WXFMR AFTAUTO1 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13944 | 111.67 | P21:161:GRDA:SILSPWW-KANSATP5:::HV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13947 | 126.59 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.14073 | 110.9 | 547579 COM381T2 69.0 547590 QUA377 2 69.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.14073 | 112.16 | 547579 COM381T2 69.0 547583 FRL363 2 69.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.14175 | 120.22 | 300852 2MIAETP 69.0 512630 MIAMI 2 69.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.14352 | 130.31 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.30444 | 126.84 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14585 | 167.35 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14585 | 168.52 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14598 | 164.02 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14598 | 164.1 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14782 | 158.09 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14809 | 158.9 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14814 | 158.54 | 547498 STL439 5 161 547657 S3G439 1 18.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14829 | 157.87 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14829 | 157.97 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14835 | 166.79 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14839 | 160.25 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14839 | 160.44 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14841 | 159.75 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14841 | 159.76 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14842 | 156.72 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14844 | 157.31 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14848 | 158.42 | P23:345:WERE:WICH-345-116:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14849 | 155.79 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14849 | 155.96 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14849 | 157.14 | P12:EHV:EES::7STFRAN!:7GOBKNOB%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14849 | 164.14 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1485 | 155.82 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1485 | 156.09 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1485 | 158.11 | 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1485 | 158.22 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1485 | 158.58 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1485 | 158.96 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1485 | 161.55 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1485 | 161.55 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14851 | 155.74 | 659348 LC_CT1-3-BE7 115 659349 LC_SWY.N-BE7 115 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14851 | 156.05 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14851 | 156.05 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14851 | 156.28 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14851 | 156.28 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14851 | 157 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14851 | 157 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14851 | 160.37 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 155.87 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 155.88 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 155.88 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 155.94 | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 156.21 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 156.26 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 156.35 | 772981 GEN-2023-050 345 772982 G23-050XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 156.35 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 156.38 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 156.62 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 156.67 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 156.82 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 156.82 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 156.87 | P23:345:XEL:8H14 PRI | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 156.88 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 156.89 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 157.04 | 771661 GEN-2022-234 138 771662 G22-234XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 157.04 | GEN-2022-234_POI_771660_Generator_outage | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 157.05 | P23:345:MEC:LOUISA 954 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 157.17 | GEN-2023-050_POI_532793_Generator_outage | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 157.23 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 157.24 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 157.24 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 157.25 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 157.36 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 157.38 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 157.39 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 157.5 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 157.59 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 157.66 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 157.71 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 157.83 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 157.83 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 157.84 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 157.87 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 157.96 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 158.04 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 158.15 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 158.16 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 158.17 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 158.4 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 158.56 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 158.68 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 159.08 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 159.28 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 159.31 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 159.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 159.67 | 764300 GEN-2020-079 161 764310 G20-079-TAP 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 159.67 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 159.67 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 163.21 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14853 | 156.24 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14853 | 156.71 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14853 | 157.56 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14853 | 157.56 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14853 | 158.35 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14853 | 158.46 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14853 | 159.31 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14853 | 159.84 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14853 | 161.55 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14854 | 156.08 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14854 | 156.33 | P23:345:AMMO::MONTGOMERY:V43:: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14854 | 156.77 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14854 | 157.94 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14855 | 156.6 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14855 | 156.63 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14855 | 156.69 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14855 | 158.12 | P12:500-161:EES-EAI:M:NEW_MAD:PORTGV:WMPEHV:8BHAMSTE:HATI_S:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14855 | 158.13 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14855 | 158.22 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14855 | 158.72 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14855 | 160.86 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14855 | 161.72 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14857 | 158.73 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1486 | 156.89 | 547561 NOL443 2 69.0 547610 NOL435 2 69.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14861 | 165.01 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14861 | 165.73 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14861 | 165.73 | P42:345:OKGE:SB_OPKY7319:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14861 | 168.39 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14861 | 170.34 | Potential P4 Event - POI 560053_1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14861 | 170.37 | Potential P4 Event - POI 560053_2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14861 | 170.43 | Potential P4 Event - POI 560053_0 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14861 | 175.56 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14863 | 157.13 | 506952 CENTRTN5 161 506980 SHIPERD5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14871 | 158.01 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14877 | 176.36 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14877 | 178.68 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14882 | 178.68 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14882 | 178.68 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1489 | 162.38 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1489 | 173.59 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1489 | 177.68 | Potential P4 Event - POI 773480_2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1489 | 177.75 | Potential P4 Event - POI 773480_1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1489 | 177.8 | Potential P4 Event - POI 773480_0 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1489 | 181.62 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1489 | 181.62 | Potential P4 Event - POI 532793_16 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1489 | 181.64 | Potential P4 Event - POI 532793_13 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1489 | 183.92 | Potential P4 Event - POI 532793_18 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14891 | 162.7 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14906 | 157.41 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14921 | 158.92 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14921 | 160.1 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14921 | 162.05 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14935 | 158.53 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14953 | 164.43 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.15097 | 170.31 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.15176 | 166.38 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.15177 | 174.39 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.15209 | 161.27 | P21:161:GRDA:SILSPWW-KANSATP5:::HV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.15271 | 181.04 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.15584 | 180.8 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.17067 | 169.8 | 512654 PENSA 5 161 3WXFMR PENAUTO1 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.34204 | 180.63 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512633 AFTON 2 69.0 512708 FAIRTAP2 69.0 1 | 72 | 72 | 0.05179 | 198.55 | P21:161:GRDA:MIAMI5-AFTON5:::HV: | Cumulative Impact | AFTON2 to FAIRTAP2 69 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14585 | 172.01 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14585 | 173.18 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14598 | 168.66 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14598 | 168.75 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14782 | 162.74 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14809 | 163.56 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14814 | 163.19 | 547498 STL439 5 161 547657 S3G439 1 18.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14829 | 162.52 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14829 | 162.62 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14835 | 171.5 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14839 | 164.93 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14839 | 165.12 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14841 | 164.41 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14841 | 164.42 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14842 | 161.36 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14844 | 161.96 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14848 | 163.07 | P23:345:WERE:WICH-345-116:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14849 | 160.43 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14849 | 160.6 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14849 | 161.79 | P12:EHV:EES::7STFRAN!:7GOBKNOB%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14849 | 168.79 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1485 | 160.46 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1485 | 160.73 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1485 | 162.78 | 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1485 | 162.87 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1485 | 163.24 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1485 | 163.62 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1485 | 166.23 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1485 | 166.23 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14851 | 160.38 | 659348 LC_CT1-3-BE7 115 659349 LC_SWY.N-BE7 115 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14851 | 160.68 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14851 | 160.69 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14851 | 160.92 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14851 | 160.92 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14851 | 161.65 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14851 | 161.65 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14851 | 165.04 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 160.51 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 160.52 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 160.52 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 160.58 | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 160.85 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 160.9 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 160.99 | 772981 GEN-2023-050 345 772985 G23-050XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 160.99 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 161.02 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 161.27 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 161.31 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 161.47 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 161.47 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 161.52 | P23:345:XEL:8H14 PRI | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 161.53 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 161.53 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 161.68 | 771661 GEN-2022-234 138 771662 G22-234XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 161.68 | GEN-2022-234_POI_771660_Generator_outage | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 161.7 | P23:345:MEC:LOUISA 954 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 161.82 | GEN-2023-050_POI_532793_Generator_outage | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 161.88 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 161.89 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 161.89 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 161.9 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 162.01 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 162.03 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 162.04 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 162.15 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 162.24 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 162.32 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 162.36 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 162.48 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 162.48 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 162.5 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 162.52 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 162.61 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 162.7 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 162.8 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 162.82 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 162.83 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 163.05 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 163.21 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 163.34 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 163.75 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 163.95 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 163.96 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 164.25 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 164.33 | 764300 GEN-2020-079 161 764310 G20-079-TAP 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 164.33 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 164.33 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14852 | 167.89 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14853 | 160.88 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14853 | 161.35 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14853 | 162.21 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14853 | 162.21 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14853 | 163.01 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14853 | 163.13 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14853 | 163.98 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14853 | 164.5 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14853 | 166.22 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14854 | 160.73 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14854 | 160.97 | P23:345:AMMO::MONTGOMERY:V43:: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14854 | 161.42 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14854 | 162.59 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14855 | 161.24 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14855 | 161.27 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14855 | 161.34 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14855 | 162.78 | P12:500-161:EES-EAI:M:NEW_MAD:PORTGV:WMPEHV:8BHAMSTE:HATI_S:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14855 | 162.78 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14855 | 162.88 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14855 | 163.38 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14855 | 165.54 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14855 | 166.4 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14857 | 163.39 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1486 | 161.54 | 547561 NOL443 2 69.0 547610 NOL435 2 69.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14861 | 169.69 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14861 | 170.4 | P42:345:OKGE:SB_OPKY7319:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14861 | 170.41 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14861 | 173.08 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14861 | 175.04 | Potential P4 Event - POI 560053_1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14861 | 175.08 | Potential P4 Event - POI 560053_2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14861 | 175.14 | Potential P4 Event - POI 560053_0 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14861 | 180.3 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14863 | 161.77 | 506952 CENTRTN5 161 506980 SHIPERD5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14871 | 162.66 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14877 | 181.05 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14877 | 183.39 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14882 | 183.39 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14882 | 183.39 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1489 | 167.08 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1489 | 178.28 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1489 | 182.39 | Potential P4 Event - POI 773480_2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1489 | 182.46 | Potential P4 Event - POI 773480_1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1489 | 182.51 | Potential P4 Event - POI 773480_0 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1489 | 186.36 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1489 | 186.36 | Potential P4 Event - POI 532793_16 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1489 | 186.38 | Potential P4 Event - POI 532793_13 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1489 | 188.67 | Potential P4 Event - POI 532793_18 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14891 | 167.37 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14906 | 162.05 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14921 | 163.57 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14921 | 164.74 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14921 | 166.71 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14935 | 163.17 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14953 | 169.09 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.15097 | 175.01 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.15176 | 171.06 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.15177 | 179.11 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.15209 | 165.93 | P21:161:GRDA:SILSPWW-KANSATP5:::HV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.15271 | 185.79 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.15584 | 185.52 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.17067 | 174.45 | 512654 PENSA 5 161 3WXFMR PENAUTO1 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.34204 | 185.33 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 0.36124 | 101.6 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 113.45 | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 134.05 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.05105 | 103.43 | P12:345:WERE:ROSE-WOLF-345:::EHV: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.05105 | 103.43 | Potential P4 Event - POI 532794_6 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.05105 | 118.12 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.05844 | 103.77 | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | 1015 | 1015 | 0.09963 | 101.92 | Potential P4 Event - POI 532794_7 | Cumulative Impact | Line - Wolf Creek - Blackberry 345 kV
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-028 | FROM->TO | 767240 G22-013-TAP 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09963 | 102.19 | Potential P4 Event - POI 532794_7 | Cumulative Impact | Line - Wolf Creek - Blackberry 345 kV
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-038 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.06209 | 113.05 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-038 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.06209 | 113.05 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-038 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.06209 | 113.05 | Potential P4 Event - POI 508359_5 | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-038 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.06573 | 103.89 | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-038 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.06573 | 103.89 | 521157 HUGO 7 345 3WXFMR HUGO 1 1 | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | 335 | 335 | 1 | 111.98 | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | Cumulative Impact | DRYGULCH5 to G23-028-TAP 161 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16256 | 151.73 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16256 | 151.8 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16341 | 150.39 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16341 | 151.53 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16501 | 156.95 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16519 | 146.55 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16523 | 146.2 | 547498 STL439 5 161 547657 S3G439 1 18.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16527 | 147.17 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16527 | 147.18 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16537 | 145.49 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16537 | 145.59 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16543 | 154.37 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16547 | 148.09 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16548 | 147.9 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16551 | 144.41 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16553 | 144.99 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16556 | 146.12 | P23:345:WERE:WICH-345-116:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16557 | 144.8 | P12:EHV:EES::7STFRAN!:7GOBKNOB%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16558 | 143.49 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16558 | 143.66 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16558 | 145.86 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16559 | 143.52 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16559 | 143.78 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16559 | 143.99 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16559 | 145.77 | 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16559 | 146.26 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16559 | 146.65 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16559 | 148.02 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16559 | 149.24 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16559 | 149.24 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1656 | 143.44 | 659348 LC_CT1-3-BE7 115 659349 LC_SWY.N-BE7 115 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1656 | 143.65 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1656 | 143.75 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1656 | 143.75 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1656 | 143.99 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1656 | 144.68 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1656 | 144.68 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1656 | 150.88 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1656 | 164.1 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1656 | 166.41 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 143.57 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 143.57 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 143.57 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 143.91 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 143.96 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 144.05 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 144.06 | 772981 GEN-2023-050 345 772982 G23-050XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 144.06 | 772981 GEN-2023-050 345 772985 G23-050XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 144.08 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 144.13 | GEN-2023-075_POI_773480_Generator_outage | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 144.31 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 144.36 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 144.39 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 144.51 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 144.51 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 144.56 | P23:345:XEL:8H14 PRI | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 144.57 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 144.57 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 144.74 | P23:345:MEC:LOUISA 954 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 144.88 | GEN-2023-050_POI_532793_Generator_outage | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 144.91 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 144.92 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 144.92 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 144.93 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 145.03 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 145.06 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 145.08 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 145.17 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 145.22 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 145.22 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 145.26 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 145.27 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 145.38 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 145.5 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 145.5 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 145.51 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 145.56 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 145.56 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 145.63 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 145.7 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 145.81 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 145.82 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 145.84 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 146.01 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 146.05 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 146.13 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 146.21 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 146.33 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 146.7 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 146.89 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 146.96 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 146.96 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 147.23 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 147.37 | 764300 GEN-2020-079 161 764310 G20-079-TAP 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 147.37 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 147.37 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 147.5 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16561 | 149.17 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16562 | 143.93 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16562 | 144.03 | P23:345:AMMO::MONTGOMERY:V43:: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16563 | 143.78 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16563 | 144.32 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16563 | 144.36 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16563 | 144.42 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16563 | 144.45 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16563 | 148.45 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16564 | 145.76 | P12:500-161:EES-EAI:M:NEW_MAD:PORTGV:WMPEHV:8BHAMSTE:HATI_S:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16564 | 145.77 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16564 | 145.86 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16564 | 146.35 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16564 | 149.28 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16565 | 146.37 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16566 | 166.4 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16566 | 166.4 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16567 | 152.71 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16567 | 153.43 | P42:345:OKGE:SB_OPKY7319:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16567 | 153.44 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16567 | 156.08 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16567 | 158.01 | Potential P4 Event - POI 560053_1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16567 | 158.04 | Potential P4 Event - POI 560053_2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16567 | 158.1 | Potential P4 Event - POI 560053_0 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16567 | 163.23 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1657 | 144.73 | 506952 CENTRTN5 161 506980 SHIPERD5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16578 | 145.6 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16578 | 161.5 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16578 | 165.61 | Potential P4 Event - POI 773480_2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16578 | 165.67 | Potential P4 Event - POI 773480_1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16578 | 165.72 | Potential P4 Event - POI 773480_0 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16578 | 169.52 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16578 | 169.52 | Potential P4 Event - POI 532793_16 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16578 | 169.54 | Potential P4 Event - POI 532793_13 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16578 | 171.81 | Potential P4 Event - POI 532793_18 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16594 | 149.56 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16594 | 150.76 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16608 | 144.99 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16615 | 146.51 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16615 | 147.65 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16615 | 149.5 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16629 | 152.05 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16641 | 146.45 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16786 | 157.58 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1681 | 145.88 | 547579 COM381T2 69.0 547583 FRL363 2 69.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16837 | 161.04 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16843 | 153.38 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16909 | 167.24 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16913 | 148.76 | P21:161:GRDA:SILSPWW-KANSATP5:::HV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.17213 | 167.59 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1758 | 150.4 | 512632 AFTON 5 161 3WXFMR AFTAUTO1 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1804 | 150.46 | 512654 PENSA 5 161 3WXFMR PENAUTO1 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.30695 | 165.54 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16059 | 111.18 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16223 | 115.99 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16223 | 116.02 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16415 | 111.68 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16415 | 112.74 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.165 | 125.71 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16543 | 109.69 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16549 | 109.39 | 547498 STL439 5 161 547657 S3G439 1 18.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16564 | 109.28 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16564 | 109.28 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16571 | 117.33 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16572 | 108.06 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16572 | 108.12 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16576 | 110.85 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1658 | 107.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16583 | 108 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16586 | 109.33 | P23:345:WERE:WICH-345-116:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16589 | 106.67 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16589 | 106.84 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16589 | 107.7 | P12:EHV:EES::7STFRAN!:7GOBKNOB%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16589 | 109.38 | 512631 MIAMI 5 161 3WXFMR MIAAUTO2 2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1659 | 106.7 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1659 | 107.02 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1659 | 108.52 | 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1659 | 108.77 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1659 | 109.39 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1659 | 110.04 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1659 | 110.83 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1659 | 112.86 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1659 | 112.86 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16591 | 106.62 | 659348 LC_CT1-3-BE7 115 659349 LC_SWY.N-BE7 115 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16591 | 106.83 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16591 | 107 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16591 | 107 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16591 | 107.14 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16591 | 107.16 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16591 | 107.88 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16591 | 107.88 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16591 | 113.99 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 106.74 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 106.77 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 106.77 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 107.11 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 107.15 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 107.22 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 107.28 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 107.36 | 772981 GEN-2023-050 345 772982 G23-050XFMR1 34.5 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 107.36 | 772981 GEN-2023-050 345 772985 G23-050XFMR2 34.5 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 107.5 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 107.6 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 107.61 | GEN-2023-075_POI_773480_Generator_outage | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 107.75 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 107.75 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 107.78 | P23:345:XEL:8H14 PRI | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 107.8 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 107.8 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 107.83 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 107.89 | P23:345:MEC:LOUISA 964 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 108.1 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 108.1 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 108.11 | P23:345:XEL:8N17 SHC | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 108.12 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 108.19 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 108.21 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 108.22 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 108.29 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 108.3 | GEN-2023-050_POI_532793_Generator_outage | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 108.3 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 108.49 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 108.6 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 108.65 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 108.68 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 108.73 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 108.73 | P23:345:MEC:CBEC 908 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 108.79 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 108.86 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 108.88 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 109.03 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 109.05 | P23:345:MEC:CBEC 905 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 109.27 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 109.29 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 109.43 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 109.43 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 109.54 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 109.96 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 110.48 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 110.79 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 110.91 | 764300 GEN-2020-079 161 764310 G20-079-TAP 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 110.91 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 110.91 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 112.8 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 128.8 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16592 | 131.04 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16593 | 107.51 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16593 | 108.28 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16593 | 108.28 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16593 | 108.83 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16593 | 109.62 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16594 | 107.21 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16594 | 107.41 | P23:345:AMMO::MONTGOMERY:V43:: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16594 | 107.49 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16594 | 111.09 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16595 | 107.06 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16595 | 107.58 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16595 | 107.61 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16595 | 107.67 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16595 | 108.74 | P12:500-161:EES-EAI:M:NEW_MAD:PORTGV:WMPEHV:8BHAMSTE:HATI_S:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16595 | 108.76 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16595 | 108.85 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16595 | 109.31 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16595 | 111.84 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16597 | 109.31 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16599 | 131.01 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16599 | 131.01 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.166 | 116.1 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.166 | 117.07 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.166 | 117.1 | P42:345:OKGE:SB_OPKY7388:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.166 | 119.43 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.166 | 121.8 | Potential P4 Event - POI 560053_1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.166 | 121.83 | Potential P4 Event - POI 560053_2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.166 | 121.88 | Potential P4 Event - POI 560053_0 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.166 | 126.78 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16607 | 108.25 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 125.84 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 130.38 | Potential P4 Event - POI 773480_2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 130.41 | Potential P4 Event - POI 773480_1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 130.46 | Potential P4 Event - POI 773480_0 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 133.88 | Potential P4 Event - POI 532793_13 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 133.89 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 133.89 | Potential P4 Event - POI 532793_16 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 136.36 | Potential P4 Event - POI 532793_18 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16615 | 107.55 | 505486 NEO SPA5 161 505488 CARTHAG5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16633 | 114.57 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16639 | 109.07 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16639 | 110.22 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16639 | 111.24 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1664 | 108.08 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16655 | 113.66 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16781 | 112.94 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16836 | 120.06 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16854 | 121.48 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16882 | 116.01 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16915 | 126.59 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16963 | 111.67 | P21:161:GRDA:SILSPWW-KANSATP5:::HV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.17032 | 109.26 | 512632 AFTON 5 161 3WXFMR AFTAUTO1 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.17178 | 110.9 | 547579 COM381T2 69.0 547590 QUA377 2 69.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.17178 | 112.16 | 547579 COM381T2 69.0 547583 FRL363 2 69.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.17304 | 130.31 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.17333 | 120.22 | 300852 2MIAETP 69.0 512630 MIAMI 2 69.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.30444 | 126.84 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.17956 | 167.35 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.17956 | 168.52 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18003 | 164.02 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18003 | 164.1 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18223 | 158.09 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18265 | 158.9 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1827 | 158.54 | 547498 STL439 5 161 547657 S3G439 1 18.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1827 | 164.14 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18271 | 159.75 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18271 | 159.76 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18283 | 157.87 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18283 | 157.97 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18289 | 166.79 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18293 | 160.44 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18294 | 160.25 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18297 | 156.72 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18299 | 157.31 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18302 | 158.42 | P23:345:WERE:WICH-345-116:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18304 | 157.14 | P12:EHV:EES::7STFRAN!:7GOBKNOB%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18305 | 155.79 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18305 | 155.96 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18305 | 158.22 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18305 | 158.58 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18306 | 155.74 | 659348 LC_CT1-3-BE7 115 659349 LC_SWY.N-BE7 115 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18306 | 155.82 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18306 | 156.05 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18306 | 156.05 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18306 | 156.09 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18306 | 156.28 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18306 | 156.28 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18306 | 158.11 | 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18306 | 158.96 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18306 | 160.37 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18306 | 161.55 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18306 | 161.55 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18306 | 163.21 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 155.87 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 155.88 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 155.88 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 155.94 | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 156.21 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 156.26 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 156.35 | 772981 GEN-2023-050 345 772982 G23-050XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 156.35 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 156.38 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 156.62 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 156.67 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 156.82 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 156.82 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 156.87 | P23:345:XEL:8H14 PRI | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 156.88 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 156.89 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 157 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 157 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 157.04 | 771661 GEN-2022-234 138 771662 G22-234XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 157.04 | GEN-2022-234_POI_771660_Generator_outage | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 157.05 | P23:345:MEC:LOUISA 954 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 157.17 | GEN-2023-050_POI_532793_Generator_outage | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 157.23 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 157.24 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 157.24 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 157.25 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 157.36 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 157.38 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 157.39 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 157.5 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 157.59 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 157.66 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 157.71 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 157.83 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 157.83 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 157.84 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 157.87 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 157.94 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 157.96 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 158.04 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 158.15 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 158.16 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 158.4 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 158.56 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 158.68 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 159.08 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 159.28 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 159.31 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 159.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 159.67 | 764300 GEN-2020-079 161 764310 G20-079-TAP 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 159.67 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 159.67 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 176.36 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 178.68 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18308 | 156.71 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18308 | 157.56 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18308 | 157.56 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18308 | 158.17 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18308 | 158.35 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18308 | 158.46 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18308 | 159.31 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18308 | 159.84 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18308 | 161.55 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18309 | 156.08 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18309 | 156.24 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18309 | 156.33 | P23:345:AMMO::MONTGOMERY:V43:: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18309 | 156.77 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1831 | 156.6 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1831 | 156.63 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1831 | 156.69 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1831 | 158.12 | P12:500-161:EES-EAI:M:NEW_MAD:PORTGV:WMPEHV:8BHAMSTE:HATI_S:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1831 | 158.13 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1831 | 158.22 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1831 | 158.72 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1831 | 160.86 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1831 | 161.72 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18312 | 156.89 | 547561 NOL443 2 69.0 547610 NOL435 2 69.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18312 | 158.73 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18312 | 178.68 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18312 | 178.68 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18314 | 165.01 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18314 | 165.73 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18314 | 165.73 | P42:345:OKGE:SB_OPKY7319:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18314 | 168.39 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18314 | 170.34 | Potential P4 Event - POI 560053_1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18314 | 170.37 | Potential P4 Event - POI 560053_2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18314 | 170.43 | Potential P4 Event - POI 560053_0 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18314 | 175.56 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18317 | 157.13 | 506952 CENTRTN5 161 506980 SHIPERD5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18324 | 173.59 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18324 | 177.68 | Potential P4 Event - POI 773480_2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18324 | 177.75 | Potential P4 Event - POI 773480_1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18324 | 177.8 | Potential P4 Event - POI 773480_0 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18324 | 181.62 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18324 | 181.62 | Potential P4 Event - POI 532793_16 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18324 | 181.64 | Potential P4 Event - POI 532793_13 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18324 | 183.92 | Potential P4 Event - POI 532793_18 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18325 | 158.01 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18338 | 162.7 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18343 | 162.38 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18358 | 157.41 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18363 | 158.92 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18363 | 160.1 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18363 | 162.05 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18376 | 164.43 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18382 | 158.53 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18538 | 170.31 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18599 | 174.39 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18609 | 166.38 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18673 | 161.27 | P21:161:GRDA:SILSPWW-KANSATP5:::HV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18677 | 181.04 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18983 | 180.8 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.2113 | 169.8 | 512654 PENSA 5 161 3WXFMR PENAUTO1 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.34204 | 180.63 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512633 AFTON 2 69.0 512708 FAIRTAP2 69.0 1 | 72 | 72 | 0.06261 | 198.55 | P21:161:GRDA:MIAMI5-AFTON5:::HV: | Cumulative Impact | AFTON2 to FAIRTAP2 69 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.17956 | 172.01 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.17956 | 173.18 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18003 | 168.66 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18003 | 168.75 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18223 | 162.74 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18265 | 163.56 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1827 | 163.19 | 547498 STL439 5 161 547657 S3G439 1 18.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1827 | 168.79 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18271 | 164.41 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18271 | 164.42 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18283 | 162.52 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18283 | 162.62 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18289 | 171.5 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18293 | 165.12 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18294 | 164.93 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18297 | 161.36 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18299 | 161.96 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18302 | 163.07 | P23:345:WERE:WICH-345-116:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18304 | 161.79 | P12:EHV:EES::7STFRAN!:7GOBKNOB%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18305 | 160.43 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18305 | 160.6 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18305 | 162.87 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18305 | 163.24 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18306 | 160.38 | 659348 LC_CT1-3-BE7 115 659349 LC_SWY.N-BE7 115 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18306 | 160.46 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18306 | 160.68 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18306 | 160.69 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18306 | 160.73 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18306 | 160.92 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18306 | 160.92 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18306 | 162.78 | 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18306 | 163.62 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18306 | 165.04 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18306 | 166.23 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18306 | 166.23 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18306 | 167.89 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 160.51 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 160.52 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 160.52 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 160.58 | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 160.85 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 160.9 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 160.99 | 772981 GEN-2023-050 345 772985 G23-050XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 160.99 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 161.02 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 161.27 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 161.31 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 161.47 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 161.47 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 161.52 | P23:345:XEL:8H14 PRI | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 161.53 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 161.53 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 161.65 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 161.65 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 161.68 | 771661 GEN-2022-234 138 771662 G22-234XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 161.68 | GEN-2022-234_POI_771660_Generator_outage | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 161.7 | P23:345:MEC:LOUISA 954 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 161.82 | GEN-2023-050_POI_532793_Generator_outage | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 161.88 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 161.89 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 161.89 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 161.9 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 162.01 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 162.03 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 162.04 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 162.15 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 162.24 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 162.32 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 162.36 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 162.48 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 162.48 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 162.5 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 162.52 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 162.59 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 162.61 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 162.7 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 162.8 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 162.82 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 163.05 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 163.21 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 163.34 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 163.75 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 163.95 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 163.96 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 164.25 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 164.33 | 764300 GEN-2020-079 161 764310 G20-079-TAP 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 164.33 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 164.33 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 181.05 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18307 | 183.39 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18308 | 161.35 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18308 | 162.21 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18308 | 162.21 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18308 | 162.83 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18308 | 163.01 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18308 | 163.13 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18308 | 163.98 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18308 | 164.5 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18308 | 166.22 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18309 | 160.73 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18309 | 160.88 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18309 | 160.97 | P23:345:AMMO::MONTGOMERY:V43:: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18309 | 161.42 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1831 | 161.24 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1831 | 161.27 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1831 | 161.34 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1831 | 162.78 | P12:500-161:EES-EAI:M:NEW_MAD:PORTGV:WMPEHV:8BHAMSTE:HATI_S:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1831 | 162.78 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1831 | 162.88 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1831 | 163.38 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1831 | 165.54 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1831 | 166.4 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18312 | 161.54 | 547561 NOL443 2 69.0 547610 NOL435 2 69.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18312 | 163.39 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18312 | 183.39 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18312 | 183.39 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18314 | 169.69 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18314 | 170.4 | P42:345:OKGE:SB_OPKY7319:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18314 | 170.41 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18314 | 173.08 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18314 | 175.04 | Potential P4 Event - POI 560053_1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18314 | 175.08 | Potential P4 Event - POI 560053_2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18314 | 175.14 | Potential P4 Event - POI 560053_0 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18314 | 180.3 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18317 | 161.77 | 506952 CENTRTN5 161 506980 SHIPERD5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18324 | 178.28 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18324 | 182.39 | Potential P4 Event - POI 773480_2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18324 | 182.46 | Potential P4 Event - POI 773480_1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18324 | 182.51 | Potential P4 Event - POI 773480_0 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18324 | 186.36 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18324 | 186.36 | Potential P4 Event - POI 532793_16 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18324 | 186.38 | Potential P4 Event - POI 532793_13 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18324 | 188.67 | Potential P4 Event - POI 532793_18 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18325 | 162.66 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18338 | 167.37 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18343 | 167.08 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18358 | 162.05 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18363 | 163.57 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18363 | 164.74 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18363 | 166.71 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18376 | 169.09 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18382 | 163.17 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18538 | 175.01 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18599 | 179.11 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18609 | 171.06 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18673 | 165.93 | P21:161:GRDA:SILSPWW-KANSATP5:::HV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18677 | 185.79 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18983 | 185.52 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.2113 | 174.45 | 512654 PENSA 5 161 3WXFMR PENAUTO1 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.34204 | 185.33 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 0.47558 | 101.6 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 113.45 | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 134.05 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.05105 | 103.43 | P12:345:WERE:ROSE-WOLF-345:::EHV: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.05105 | 103.43 | Potential P4 Event - POI 532794_6 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.05105 | 118.12 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.0589 | 103.77 | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | 1015 | 1015 | 0.10135 | 101.92 | Potential P4 Event - POI 532794_7 | Cumulative Impact | Line - Wolf Creek - Blackberry 345 kV
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-049 | FROM->TO | 767240 G22-013-TAP 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10135 | 102.19 | Potential P4 Event - POI 532794_7 | Cumulative Impact | Line - Wolf Creek - Blackberry 345 kV
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06026 | 151.73 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06026 | 151.8 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06081 | 165.54 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06114 | 150.39 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06114 | 151.53 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06129 | 146.55 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06134 | 146.2 | 547498 STL439 5 161 547657 S3G439 1 18.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.0615 | 145.49 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.0615 | 145.59 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06157 | 154.37 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06159 | 148.09 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.0616 | 147.9 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06161 | 144.41 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06164 | 144.99 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06168 | 144.8 | P12:EHV:EES::7STFRAN!:7GOBKNOB%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06168 | 146.12 | P23:345:WERE:WICH-345-116:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06169 | 143.49 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06169 | 143.66 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.0617 | 143.44 | 659348 LC_CT1-3-BE7 115 659349 LC_SWY.N-BE7 115 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.0617 | 143.52 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.0617 | 143.78 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.0617 | 143.99 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.0617 | 145.77 | 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.0617 | 146.26 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.0617 | 146.65 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.0617 | 149.24 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.0617 | 149.24 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 143.57 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 143.57 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 143.65 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 143.75 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 143.75 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 143.91 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 143.96 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 143.99 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 144.05 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 144.06 | 772981 GEN-2023-050 345 772982 G23-050XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 144.06 | 772981 GEN-2023-050 345 772985 G23-050XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 144.13 | GEN-2023-075_POI_773480_Generator_outage | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 144.31 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 144.36 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 144.51 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 144.51 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 144.56 | P23:345:XEL:8H14 PRI | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 144.57 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 144.57 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 144.68 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 144.68 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 144.88 | GEN-2023-050_POI_532793_Generator_outage | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 144.91 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 144.92 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 144.92 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 144.93 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 145.03 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 145.06 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 145.17 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 145.26 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 145.27 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 145.38 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 145.5 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 145.5 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 145.51 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 145.63 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 145.7 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 145.81 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 145.82 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 146.05 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 146.21 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 146.33 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 146.7 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 146.89 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 146.96 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 147.37 | 764300 GEN-2020-079 161 764310 G20-079-TAP 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 147.37 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 147.37 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06171 | 148.02 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06172 | 143.57 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06172 | 144.08 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06172 | 144.39 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06172 | 144.74 | P23:345:MEC:LOUISA 954 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06172 | 145.08 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06172 | 145.22 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06172 | 145.22 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06172 | 145.56 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06172 | 145.84 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06172 | 145.86 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06172 | 146.01 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06172 | 146.13 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06172 | 146.96 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06172 | 147.23 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06172 | 149.17 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06173 | 143.78 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06173 | 143.93 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06173 | 144.03 | P23:345:AMMO::MONTGOMERY:V43:: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06173 | 144.45 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06173 | 147.5 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06174 | 150.88 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06175 | 144.32 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06175 | 144.36 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06175 | 144.42 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06175 | 145.76 | P12:500-161:EES-EAI:M:NEW_MAD:PORTGV:WMPEHV:8BHAMSTE:HATI_S:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06175 | 145.77 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06175 | 145.86 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06175 | 146.35 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06176 | 148.45 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06176 | 149.28 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06177 | 146.37 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06179 | 145.56 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06182 | 144.73 | 506952 CENTRTN5 161 506980 SHIPERD5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06187 | 152.71 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06187 | 153.43 | P42:345:OKGE:SB_OPKY7319:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06187 | 153.44 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06187 | 156.08 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06187 | 158.01 | Potential P4 Event - POI 560053_1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06187 | 158.04 | Potential P4 Event - POI 560053_2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06187 | 158.1 | Potential P4 Event - POI 560053_0 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06187 | 163.23 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06192 | 145.6 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06207 | 149.56 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06215 | 147.17 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06215 | 147.18 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06225 | 144.99 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06231 | 150.76 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.0625 | 164.1 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.0625 | 166.41 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06255 | 161.5 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06255 | 165.61 | Potential P4 Event - POI 773480_2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06255 | 165.67 | Potential P4 Event - POI 773480_1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06255 | 165.72 | Potential P4 Event - POI 773480_0 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06255 | 169.52 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06255 | 169.52 | Potential P4 Event - POI 532793_16 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06255 | 169.54 | Potential P4 Event - POI 532793_13 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06255 | 171.81 | Potential P4 Event - POI 532793_18 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06258 | 166.4 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06258 | 166.4 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06278 | 146.51 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06278 | 147.65 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06278 | 149.5 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06287 | 145.88 | 547579 COM381T2 69.0 547583 FRL363 2 69.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06299 | 156.95 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06302 | 146.45 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06386 | 152.05 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06416 | 150.4 | 512632 AFTON 5 161 3WXFMR AFTAUTO1 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06459 | 157.58 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06491 | 153.38 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06499 | 161.04 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06543 | 167.24 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06551 | 150.46 | 512654 PENSA 5 161 3WXFMR PENAUTO1 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06771 | 148.76 | P21:161:GRDA:SILSPWW-KANSATP5:::HV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06965 | 167.59 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06183 | 111.18 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06285 | 115.99 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06285 | 116.02 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06371 | 126.84 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06411 | 109.69 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06414 | 111.68 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06414 | 112.74 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06417 | 109.39 | 547498 STL439 5 161 547657 S3G439 1 18.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06428 | 109.38 | 512631 MIAMI 5 161 3WXFMR MIAAUTO2 2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06443 | 108.06 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06443 | 108.12 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06444 | 117.33 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06446 | 110.85 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06448 | 107.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06452 | 108 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06456 | 109.33 | P23:345:WERE:WICH-345-116:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06457 | 106.67 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06457 | 106.84 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06457 | 107.7 | P12:EHV:EES::7STFRAN!:7GOBKNOB%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06458 | 106.7 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06458 | 107.02 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06458 | 109.39 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06458 | 110.04 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06458 | 112.86 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06458 | 112.86 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06459 | 106.62 | 659348 LC_CT1-3-BE7 115 659349 LC_SWY.N-BE7 115 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06459 | 106.83 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06459 | 107 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06459 | 107 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06459 | 107.14 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06459 | 107.16 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06459 | 107.88 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06459 | 107.88 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06459 | 108.52 | 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06459 | 110.83 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 106.74 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 106.77 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 106.77 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 107.11 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 107.15 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 107.22 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 107.28 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 107.36 | 772981 GEN-2023-050 345 772982 G23-050XFMR1 34.5 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 107.36 | 772981 GEN-2023-050 345 772985 G23-050XFMR2 34.5 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 107.5 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 107.6 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 107.61 | GEN-2023-075_POI_773480_Generator_outage | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 107.75 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 107.75 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 107.78 | P23:345:XEL:8H14 PRI | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 107.8 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 107.8 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 107.83 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 107.89 | P23:345:MEC:LOUISA 964 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 108.1 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 108.1 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 108.11 | P23:345:XEL:8N17 SHC | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 108.12 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 108.19 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 108.22 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 108.3 | GEN-2023-050_POI_532793_Generator_outage | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 108.3 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 108.49 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 108.6 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 108.68 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 108.73 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 108.73 | P23:345:MEC:CBEC 908 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 108.86 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 108.88 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 109.03 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 109.05 | P23:345:MEC:CBEC 905 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 109.27 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 109.29 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 109.43 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 109.43 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 109.54 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 110.79 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 110.91 | 764300 GEN-2020-079 161 764310 G20-079-TAP 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 110.91 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 110.91 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 107.51 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 108.21 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 108.28 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 108.28 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 108.65 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 108.77 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 108.79 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 108.83 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 109.62 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 109.96 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 112.8 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06462 | 107.49 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06462 | 110.48 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06463 | 107.06 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06463 | 107.21 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06463 | 107.41 | P23:345:AMMO::MONTGOMERY:V43:: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06464 | 107.58 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06464 | 107.61 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06464 | 107.67 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06464 | 108.74 | P12:500-161:EES-EAI:M:NEW_MAD:PORTGV:WMPEHV:8BHAMSTE:HATI_S:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06464 | 108.76 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06464 | 108.85 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06464 | 109.31 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06464 | 113.99 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06465 | 111.09 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06465 | 111.84 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06466 | 109.31 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06467 | 108.29 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06478 | 108.25 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06478 | 116.1 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06478 | 117.07 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06478 | 117.1 | P42:345:OKGE:SB_OPKY7388:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06478 | 119.43 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06478 | 121.8 | Potential P4 Event - POI 560053_1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06478 | 121.83 | Potential P4 Event - POI 560053_2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06478 | 121.88 | Potential P4 Event - POI 560053_0 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06478 | 126.78 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0649 | 107.55 | 505486 NEO SPA5 161 505488 CARTHAG5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06496 | 109.28 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06496 | 109.28 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06515 | 108.08 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06532 | 114.57 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06552 | 109.07 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06552 | 110.22 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06552 | 111.24 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06552 | 128.8 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06552 | 131.04 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06558 | 125.84 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06558 | 130.38 | Potential P4 Event - POI 773480_2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06558 | 130.41 | Potential P4 Event - POI 773480_1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06558 | 130.46 | Potential P4 Event - POI 773480_0 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06558 | 133.88 | Potential P4 Event - POI 532793_13 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06558 | 133.89 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06558 | 133.89 | Potential P4 Event - POI 532793_16 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06558 | 136.36 | Potential P4 Event - POI 532793_18 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06561 | 131.01 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06561 | 131.01 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06566 | 109.26 | 512632 AFTON 5 161 3WXFMR AFTAUTO1 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06656 | 113.66 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06656 | 125.71 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06685 | 120.22 | 300852 2MIAETP 69.0 512630 MIAMI 2 69.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06732 | 110.9 | 547579 COM381T2 69.0 547590 QUA377 2 69.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06732 | 112.16 | 547579 COM381T2 69.0 547583 FRL363 2 69.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06767 | 112.94 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06771 | 121.48 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06772 | 120.06 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06788 | 116.01 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06805 | 126.59 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.07093 | 111.67 | P21:161:GRDA:SILSPWW-KANSATP5:::HV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.07327 | 130.31 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06446 | 164.02 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06446 | 164.1 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06489 | 180.63 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.065 | 167.35 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.065 | 168.52 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06548 | 158.9 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06552 | 158.09 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06553 | 158.54 | 547498 STL439 5 161 547657 S3G439 1 18.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06569 | 157.87 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06569 | 157.97 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06576 | 166.79 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06578 | 160.44 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06579 | 160.25 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06581 | 156.72 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06584 | 157.31 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06588 | 155.79 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06588 | 155.96 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06588 | 157.14 | P12:EHV:EES::7STFRAN!:7GOBKNOB%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06588 | 158.42 | P23:345:WERE:WICH-345-116:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06589 | 155.82 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06589 | 156.09 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06589 | 156.28 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06589 | 158.58 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06589 | 158.96 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06589 | 161.55 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06589 | 161.55 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0659 | 155.74 | 659348 LC_CT1-3-BE7 115 659349 LC_SWY.N-BE7 115 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0659 | 156.05 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0659 | 156.05 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0659 | 156.28 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0659 | 157 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0659 | 157 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0659 | 158.11 | 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0659 | 160.37 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 155.87 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 155.88 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 155.88 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 155.94 | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 156.21 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 156.26 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 156.35 | 772981 GEN-2023-050 345 772982 G23-050XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 156.35 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 156.38 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 156.62 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 156.67 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 156.82 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 156.82 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 156.87 | P23:345:XEL:8H14 PRI | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 156.88 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 156.89 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 157.04 | 771661 GEN-2022-234 138 771662 G22-234XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 157.04 | GEN-2022-234_POI_771660_Generator_outage | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 157.05 | P23:345:MEC:LOUISA 954 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 157.17 | GEN-2023-050_POI_532793_Generator_outage | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 157.23 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 157.24 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 157.24 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 157.25 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 157.36 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 157.38 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 157.39 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 157.5 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 157.59 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 157.66 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 157.71 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 157.83 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 157.83 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 157.84 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 157.87 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 157.96 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 158.04 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 158.15 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 158.16 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 158.17 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 158.22 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 158.4 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 158.56 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 158.68 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 159.08 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 159.28 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 159.31 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 159.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 159.67 | 764300 GEN-2020-079 161 764310 G20-079-TAP 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 159.67 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 159.67 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06592 | 156.08 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06592 | 156.24 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06592 | 156.71 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06592 | 157.56 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06592 | 157.56 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06592 | 158.35 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06592 | 158.46 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06592 | 159.31 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06592 | 159.84 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06592 | 161.55 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06593 | 156.33 | P23:345:AMMO::MONTGOMERY:V43:: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06593 | 156.77 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06594 | 156.6 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06594 | 156.63 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06594 | 156.69 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06594 | 158.12 | P12:500-161:EES-EAI:M:NEW_MAD:PORTGV:WMPEHV:8BHAMSTE:HATI_S:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06594 | 158.13 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06594 | 158.22 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06594 | 163.21 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06595 | 158.72 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06595 | 160.86 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06596 | 158.73 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06596 | 161.72 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06599 | 157.94 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06603 | 157.13 | 506952 CENTRTN5 161 506980 SHIPERD5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06606 | 165.01 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06606 | 165.73 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06606 | 165.73 | P42:345:OKGE:SB_OPKY7319:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06606 | 168.39 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06606 | 170.34 | Potential P4 Event - POI 560053_1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06606 | 170.37 | Potential P4 Event - POI 560053_2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06606 | 170.43 | Potential P4 Event - POI 560053_0 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06606 | 175.56 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06611 | 156.89 | 547561 NOL443 2 69.0 547610 NOL435 2 69.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06613 | 158.01 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0663 | 162.38 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06637 | 159.75 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06637 | 159.76 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06646 | 162.7 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06648 | 157.41 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06669 | 176.36 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06669 | 178.68 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0667 | 164.14 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06673 | 173.59 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06673 | 177.68 | Potential P4 Event - POI 773480_2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06673 | 177.75 | Potential P4 Event - POI 773480_1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06673 | 177.8 | Potential P4 Event - POI 773480_0 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06673 | 181.62 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06673 | 181.62 | Potential P4 Event - POI 532793_16 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06673 | 181.64 | Potential P4 Event - POI 532793_13 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06673 | 183.92 | Potential P4 Event - POI 532793_18 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06676 | 178.68 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06676 | 178.68 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06701 | 158.92 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06701 | 160.1 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06701 | 162.05 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06711 | 158.53 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06806 | 164.43 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06885 | 170.31 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06931 | 166.38 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06937 | 174.39 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06986 | 181.04 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.07214 | 161.27 | P21:161:GRDA:SILSPWW-KANSATP5:::HV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.07315 | 169.8 | 512654 PENSA 5 161 3WXFMR PENAUTO1 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.07413 | 180.8 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06446 | 168.66 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06446 | 168.75 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06489 | 185.33 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.065 | 172.01 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.065 | 173.18 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06548 | 163.56 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06552 | 162.74 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06553 | 163.19 | 547498 STL439 5 161 547657 S3G439 1 18.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06569 | 162.52 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06569 | 162.62 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06576 | 171.5 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06578 | 165.12 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06579 | 164.93 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06581 | 161.36 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06584 | 161.96 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06588 | 160.43 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06588 | 160.6 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06588 | 161.79 | P12:EHV:EES::7STFRAN!:7GOBKNOB%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06588 | 163.07 | P23:345:WERE:WICH-345-116:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06589 | 160.46 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06589 | 160.73 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06589 | 160.92 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06589 | 163.24 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06589 | 163.62 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06589 | 166.23 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06589 | 166.23 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0659 | 160.38 | 659348 LC_CT1-3-BE7 115 659349 LC_SWY.N-BE7 115 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0659 | 160.68 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0659 | 160.69 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0659 | 160.92 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0659 | 161.65 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0659 | 161.65 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0659 | 162.78 | 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0659 | 165.04 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 160.51 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 160.52 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 160.52 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 160.58 | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 160.85 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 160.9 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 160.99 | 772981 GEN-2023-050 345 772985 G23-050XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 160.99 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 161.02 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 161.27 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 161.31 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 161.47 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 161.47 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 161.52 | P23:345:XEL:8H14 PRI | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 161.53 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 161.53 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 161.68 | 771661 GEN-2022-234 138 771662 G22-234XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 161.68 | GEN-2022-234_POI_771660_Generator_outage | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 161.7 | P23:345:MEC:LOUISA 954 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 161.82 | GEN-2023-050_POI_532793_Generator_outage | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 161.88 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 161.89 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 161.89 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 161.9 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 162.01 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 162.03 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 162.04 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 162.15 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 162.24 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 162.32 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 162.36 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 162.48 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 162.48 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 162.5 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 162.52 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 162.61 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 162.7 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 162.8 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 162.82 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 162.83 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 162.87 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 163.05 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 163.21 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 163.34 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 163.75 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 163.95 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 163.96 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 164.25 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 164.33 | 764300 GEN-2020-079 161 764310 G20-079-TAP 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 164.33 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 164.33 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06592 | 160.73 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06592 | 160.88 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06592 | 161.35 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06592 | 162.21 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06592 | 162.21 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06592 | 163.01 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06592 | 163.13 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06592 | 163.98 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06592 | 164.5 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06592 | 166.22 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06593 | 160.97 | P23:345:AMMO::MONTGOMERY:V43:: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06593 | 161.42 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06594 | 161.24 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06594 | 161.27 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06594 | 161.34 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06594 | 162.78 | P12:500-161:EES-EAI:M:NEW_MAD:PORTGV:WMPEHV:8BHAMSTE:HATI_S:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06594 | 162.78 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06594 | 162.88 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06594 | 167.89 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06595 | 163.38 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06595 | 165.54 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06596 | 163.39 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06596 | 166.4 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06599 | 162.59 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06603 | 161.77 | 506952 CENTRTN5 161 506980 SHIPERD5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06606 | 169.69 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06606 | 170.4 | P42:345:OKGE:SB_OPKY7319:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06606 | 170.41 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06606 | 173.08 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06606 | 175.04 | Potential P4 Event - POI 560053_1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06606 | 175.08 | Potential P4 Event - POI 560053_2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06606 | 175.14 | Potential P4 Event - POI 560053_0 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06606 | 180.3 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06611 | 161.54 | 547561 NOL443 2 69.0 547610 NOL435 2 69.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06613 | 162.66 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0663 | 167.08 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06637 | 164.41 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06637 | 164.42 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06646 | 167.37 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06648 | 162.05 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06669 | 181.05 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06669 | 183.39 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0667 | 168.79 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06673 | 178.28 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06673 | 182.39 | Potential P4 Event - POI 773480_2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06673 | 182.46 | Potential P4 Event - POI 773480_1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06673 | 182.51 | Potential P4 Event - POI 773480_0 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06673 | 186.36 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06673 | 186.36 | Potential P4 Event - POI 532793_16 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06673 | 186.38 | Potential P4 Event - POI 532793_13 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06673 | 188.67 | Potential P4 Event - POI 532793_18 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06676 | 183.39 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06676 | 183.39 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06701 | 163.57 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06701 | 164.74 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06701 | 166.71 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06711 | 163.17 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06806 | 169.09 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06885 | 175.01 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06931 | 171.06 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06937 | 179.11 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06986 | 185.79 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.07214 | 165.93 | P21:161:GRDA:SILSPWW-KANSATP5:::HV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.07315 | 174.45 | 512654 PENSA 5 161 3WXFMR PENAUTO1 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.07413 | 185.52 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.05071 | 103.43 | P12:345:WERE:ROSE-WOLF-345:::EHV: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.05071 | 103.43 | Potential P4 Event - POI 532794_6 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.05071 | 118.12 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.05717 | 103.77 | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | 1015 | 1015 | 0.09535 | 101.92 | Potential P4 Event - POI 532794_7 | Cumulative Impact | Line - Wolf Creek - Blackberry 345 kV
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-055 | FROM->TO | 767240 G22-013-TAP 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09535 | 102.19 | Potential P4 Event - POI 532794_7 | Cumulative Impact | Line - Wolf Creek - Blackberry 345 kV
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-057 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.05207 | 103.77 | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-057 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.05948 | 103.43 | P12:345:WERE:ROSE-WOLF-345:::EHV: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-057 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.05948 | 103.43 | Potential P4 Event - POI 532794_6 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-057 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.05948 | 118.12 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-057 | FROM->TO | 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | 1015 | 1015 | 0.05627 | 101.92 | Potential P4 Event - POI 532794_7 | Cumulative Impact | Line - Wolf Creek - Blackberry 345 kV
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-057 | FROM->TO | 767240 G22-013-TAP 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.05627 | 102.19 | Potential P4 Event - POI 532794_7 | Cumulative Impact | Line - Wolf Creek - Blackberry 345 kV
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-063 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.0538 | 103.43 | P12:345:WERE:ROSE-WOLF-345:::EHV: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-063 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.0538 | 103.43 | Potential P4 Event - POI 532794_6 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-063 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.0538 | 118.12 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-063 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.05595 | 103.77 | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-063 | FROM->TO | 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | 1015 | 1015 | 0.08651 | 101.92 | Potential P4 Event - POI 532794_7 | Cumulative Impact | Line - Wolf Creek - Blackberry 345 kV
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-063 | FROM->TO | 767240 G22-013-TAP 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08651 | 102.19 | Potential P4 Event - POI 532794_7 | Cumulative Impact | Line - Wolf Creek - Blackberry 345 kV
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-064 | FROM->TO | 507189 NHUNTNT5 161 775580 G23-180-TAP 161 1 | 158 | 178 | 0.10284 | 101.01 | 515261 BONANZT5 161 515299 BEVYTAP5 161 1 | Cumulative Impact | Rebuild the existing NHUNTNT5 to G23-180-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-069 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.08074 | 113.05 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-069 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.08074 | 113.05 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-069 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.08074 | 113.05 | Potential P4 Event - POI 508359_5 | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-069 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.07794 | 101.11 | P23:345:AEPW:VALLIANT CB 3413A NBTB:::: | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-069 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.07794 | 101.11 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT:::: | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-069 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.07941 | 102.47 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-069 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.12383 | 103.89 | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-069 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.12383 | 103.89 | 521157 HUGO 7 345 3WXFMR HUGO 1 1 | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-075 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.07348 | 103.43 | P12:345:WERE:ROSE-WOLF-345:::EHV: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-075 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.07348 | 103.43 | Potential P4 Event - POI 532794_6 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-075 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.07348 | 118.12 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-075 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.08826 | 103.77 | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-075 | FROM->TO | 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | 1015 | 1015 | 0.20042 | 101.92 | Potential P4 Event - POI 532794_7 | Cumulative Impact | Line - Wolf Creek - Blackberry 345 kV
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-075 | FROM->TO | 767240 G22-013-TAP 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.20042 | 102.19 | Potential P4 Event - POI 532794_7 | Cumulative Impact | Line - Wolf Creek - Blackberry 345 kV
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-076 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.07348 | 103.43 | P12:345:WERE:ROSE-WOLF-345:::EHV: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-076 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.07348 | 103.43 | Potential P4 Event - POI 532794_6 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-076 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.07348 | 118.12 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-076 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.08826 | 103.77 | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-076 | FROM->TO | 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | 1015 | 1015 | 0.20042 | 101.92 | Potential P4 Event - POI 532794_7 | Cumulative Impact | Line - Wolf Creek - Blackberry 345 kV
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-076 | FROM->TO | 767240 G22-013-TAP 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.20042 | 102.19 | Potential P4 Event - POI 532794_7 | Cumulative Impact | Line - Wolf Creek - Blackberry 345 kV
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-088 | FROM->TO | 510898 OKMULGE4 138 510923 EC.HEN-4 138 1 | 152 | 152 | 0.15031 | 101.94 | P12:138:AEPW:HENRYET4:WELETK4::: | Cumulative Impact | OKMULGE to ECHEN4 Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-088 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.15031 | 104.71 | P12:138:AEPW:HENRYET4:WELETK4::: | Cumulative Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-088 | FROM->TO | 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | 1015 | 1015 | 0.05052 | 101.92 | Potential P4 Event - POI 532794_7 | Cumulative Impact | Line - Wolf Creek - Blackberry 345 kV
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-088 | FROM->TO | 767240 G22-013-TAP 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.05052 | 102.19 | Potential P4 Event - POI 532794_7 | Cumulative Impact | Line - Wolf Creek - Blackberry 345 kV
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-092 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.1562 | 113.05 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-092 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.1562 | 113.05 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-092 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.1562 | 113.05 | Potential P4 Event - POI 508359_5 | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-092 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.26575 | 101.11 | P23:345:AEPW:VALLIANT CB 3413A NBTB:::: | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-092 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.26575 | 101.11 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT:::: | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-092 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.26787 | 102.47 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-092 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.42496 | 103.89 | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-092 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.42496 | 103.89 | 521157 HUGO 7 345 3WXFMR HUGO 1 1 | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 435 | 435 | 1 | 108.76 | 523777 WHEELER 6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-101 | FROM->TO | 523777 WHEELER 6 230 774000 G23-101-TAP 230 1 | 353 | 353 | 1 | 135.1 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing WHEELER 6 to G23-101-TAP 230 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.68747 | 141.7 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.68747 | 141.7 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.68747 | 141.7 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.70671 | 109.01 | Potential P4 Event - POI 515852_8 | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.70671 | 109.02 | Potential P4 Event - POI 515852_4 | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.7068 | 102.56 | Potential P4 Event - POI 515375_27 | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.7068 | 102.56 | Potential P4 Event - POI 515375_36 | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.70944 | 107.72 | P42:345:OKGE:SB_REOW7312:::: | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.70944 | 107.72 | Potential P4 Event - POI 515543_0 | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.70957 | 107.01 | P12:345:OKGE:BKRBKR421:::: | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.70957 | 107.86 | Potential P4 Event - POI 515543_1 | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.70998 | 106.64 | Potential P4 Event - POI 514715_2 | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.71101 | 100.01 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.71101 | 103.55 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.71155 | 100.82 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-132 | FROM->TO | 338758 5HEBER.N# 161 505422 GREERSF5 161 1 | 205 | 205 | 1 | 109.15 | 505418 JONESBO5 161 774620 G23-132-TAP 161 1 | Cumulative Impact | Rebuild the existing 5HEBER.N# to GREERSF5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-134 | FROM->TO | 510898 OKMULGE4 138 510923 EC.HEN-4 138 1 | 152 | 152 | 0.13401 | 101.94 | P12:138:AEPW:HENRYET4:WELETK4::: | Cumulative Impact | OKMULGE to ECHEN4 Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-134 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.13401 | 104.71 | P12:138:AEPW:HENRYET4:WELETK4::: | Cumulative Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-134 | FROM->TO | 515077 FIXICO 2 69.0 997805 FIXICO4 69.0 4 | 62 | 67 | 0.20913 | 110.5 | 510902 WELETK4 138 774660 G23-134-TAP 138 1 | Cumulative Impact | Upgrade the existing FIXICO4 138/69 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-134 | FROM->TO | 515078 FIXICO 4 138 997805 FIXICO4 69.0 4 | 62 | 67 | 0.20913 | 109.05 | 510902 WELETK4 138 774660 G23-134-TAP 138 1 | Cumulative Impact | Upgrade the existing FIXICO4 138/69 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-135 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.28893 | 113.05 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-135 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.28893 | 113.05 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-135 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.28893 | 113.05 | Potential P4 Event - POI 508359_5 | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-138 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.05731 | 103.77 | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-138 | FROM->TO | 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | 1015 | 1015 | 0.09599 | 101.92 | Potential P4 Event - POI 532794_7 | Cumulative Impact | Line - Wolf Creek - Blackberry 345 kV
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-138 | FROM->TO | 767240 G22-013-TAP 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09599 | 102.19 | Potential P4 Event - POI 532794_7 | Cumulative Impact | Line - Wolf Creek - Blackberry 345 kV
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-151 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.10076 | 113.05 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-151 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.10076 | 113.05 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-151 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.10076 | 113.05 | Potential P4 Event - POI 508359_5 | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-180 | FROM->TO | 507189 NHUNTNT5 161 775580 G23-180-TAP 161 1 | 158 | 178 | 0.58964 | 101.01 | 515261 BONANZT5 161 515299 BEVYTAP5 161 1 | Cumulative Impact | Rebuild the existing NHUNTNT5 to G23-180-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-205 | FROM->TO | 510898 OKMULGE4 138 510923 EC.HEN-4 138 1 | 152 | 152 | 0.16273 | 101.94 | P12:138:AEPW:HENRYET4:WELETK4::: | Cumulative Impact | OKMULGE to ECHEN4 Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-205 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.16273 | 104.71 | P12:138:AEPW:HENRYET4:WELETK4::: | Cumulative Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-210 | FROM->TO | 510898 OKMULGE4 138 510923 EC.HEN-4 138 1 | 152 | 152 | 0.0606 | 101.94 | P12:138:AEPW:HENRYET4:WELETK4::: | Cumulative Impact | OKMULGE to ECHEN4 Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-210 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.0606 | 104.71 | P12:138:AEPW:HENRYET4:WELETK4::: | Cumulative Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 514803 SOONER 7 345 515576 RANCHRD7 345 1 | 1716 | 1793 | 1 | 101.65 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 514803 SOONER 7 345 515576 RANCHRD7 345 1 | 1716 | 1793 | 1 | 101.68 | Potential P4 Event - POI 532794_5 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 514803 SOONER 7 345 515576 RANCHRD7 345 1 | 1716 | 1793 | 1 | 101.69 | Potential P4 Event - POI 532794_2 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 514803 SOONER 7 345 515576 RANCHRD7 345 1 | 1716 | 1793 | 1 | 101.73 | Potential P4 Event - POI 532794_7 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.17948 | 103.77 | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.21093 | 103.43 | P12:345:WERE:ROSE-WOLF-345:::EHV: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.21093 | 103.43 | Potential P4 Event - POI 532794_6 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-211 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.21093 | 118.12 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-212 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.25635 | 113.05 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-212 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.25635 | 113.05 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-212 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.25635 | 113.05 | Potential P4 Event - POI 508359_5 | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-213 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.05304 | 103.77 | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-213 | FROM->TO | 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | 1015 | 1015 | 0.08736 | 101.92 | Potential P4 Event - POI 532794_7 | Cumulative Impact | Line - Wolf Creek - Blackberry 345 kV
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-213 | FROM->TO | 767240 G22-013-TAP 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08736 | 102.19 | Potential P4 Event - POI 532794_7 | Cumulative Impact | Line - Wolf Creek - Blackberry 345 kV
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-227 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.12556 | 113.05 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-227 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.12556 | 113.05 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 24SP | GEN-2023-227 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.12556 | 113.05 | Potential P4 Event - POI 508359_5 | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27L | GEN-2023-088 | FROM->TO | 505590 WELEETK5 161 998044 WLK X1 138 1 | 120 | 120 | 0.08295 | 104.07 | Potential P4 Event - POI 588839_5 | Cumulative Impact | Upgrade the existing WLK X1 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27L | GEN-2023-088 | FROM->TO | 505590 WELEETK5 161 998044 WLK X1 138 1 | 120 | 120 | 0.08316 | 103.54 | Potential P4 Event - POI 588839_1 | Cumulative Impact | Upgrade the existing WLK X1 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27L | GEN-2023-088 | FROM->TO | 505590 WELEETK5 161 998044 WLK X1 138 1 | 120 | 120 | 0.08353 | 101.79 | P42:345:OKGE:SB_FTTH7386:::: | Cumulative Impact | Upgrade the existing WLK X1 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27L | GEN-2023-088 | FROM->TO | 505590 WELEETK5 161 998044 WLK X1 138 1 | 120 | 120 | 0.08358 | 101.88 | P12:345:OKGE:BKRBKR295:::: | Cumulative Impact | Upgrade the existing WLK X1 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27L | GEN-2023-088 | FROM->TO | 505590 WELEETK5 161 998044 WLK X1 138 1 | 120 | 120 | 0.08358 | 101.88 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1 | Cumulative Impact | Upgrade the existing WLK X1 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27L | GEN-2023-088 | FROM->TO | 505590 WELEETK5 161 998044 WLK X1 138 1 | 120 | 120 | 0.08358 | 101.88 | P41:345:OKGE:SB_MUGE7385:::: | Cumulative Impact | Upgrade the existing WLK X1 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27L | GEN-2023-088 | FROM->TO | 505590 WELEETK5 161 998044 WLK X1 138 1 | 120 | 120 | 0.10017 | 106.09 | 301551 4CHECOTA 138 505592 WELEETK4 138 1 | Cumulative Impact | Upgrade the existing WLK X1 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27L | GEN-2023-088 | FROM->TO | 505592 WELEETK4 138 998044 WLK X1 138 1 | 120 | 120 | 0.08295 | 103.69 | Potential P4 Event - POI 588839_5 | Cumulative Impact | Upgrade the existing WLK X1 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27L | GEN-2023-088 | FROM->TO | 505592 WELEETK4 138 998044 WLK X1 138 1 | 120 | 120 | 0.08316 | 103.13 | Potential P4 Event - POI 588839_1 | Cumulative Impact | Upgrade the existing WLK X1 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27L | GEN-2023-088 | FROM->TO | 505592 WELEETK4 138 998044 WLK X1 138 1 | 120 | 120 | 0.08353 | 101.73 | P42:345:OKGE:SB_FTTH7386:::: | Cumulative Impact | Upgrade the existing WLK X1 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27L | GEN-2023-088 | FROM->TO | 505592 WELEETK4 138 998044 WLK X1 138 1 | 120 | 120 | 0.08358 | 101.81 | P12:345:OKGE:BKRBKR295:::: | Cumulative Impact | Upgrade the existing WLK X1 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27L | GEN-2023-088 | FROM->TO | 505592 WELEETK4 138 998044 WLK X1 138 1 | 120 | 120 | 0.08358 | 101.81 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1 | Cumulative Impact | Upgrade the existing WLK X1 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27L | GEN-2023-088 | FROM->TO | 505592 WELEETK4 138 998044 WLK X1 138 1 | 120 | 120 | 0.08358 | 101.81 | P41:345:OKGE:SB_MUGE7385:::: | Cumulative Impact | Upgrade the existing WLK X1 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27L | GEN-2023-088 | FROM->TO | 505592 WELEETK4 138 998044 WLK X1 138 1 | 120 | 120 | 0.10017 | 105.85 | 301551 4CHECOTA 138 505592 WELEETK4 138 1 | Cumulative Impact | Upgrade the existing WLK X1 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27L | GEN-2023-134 | FROM->TO | 505590 WELEETK5 161 998044 WLK X1 138 1 | 120 | 120 | 0.0507 | 101.79 | P42:345:OKGE:SB_FTTH7386:::: | Cumulative Impact | Upgrade the existing WLK X1 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27L | GEN-2023-134 | FROM->TO | 505590 WELEETK5 161 998044 WLK X1 138 1 | 120 | 120 | 0.05074 | 101.88 | P12:345:OKGE:BKRBKR295:::: | Cumulative Impact | Upgrade the existing WLK X1 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27L | GEN-2023-134 | FROM->TO | 505590 WELEETK5 161 998044 WLK X1 138 1 | 120 | 120 | 0.05074 | 101.88 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1 | Cumulative Impact | Upgrade the existing WLK X1 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27L | GEN-2023-134 | FROM->TO | 505590 WELEETK5 161 998044 WLK X1 138 1 | 120 | 120 | 0.05074 | 101.88 | P41:345:OKGE:SB_MUGE7385:::: | Cumulative Impact | Upgrade the existing WLK X1 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27L | GEN-2023-134 | FROM->TO | 505590 WELEETK5 161 998044 WLK X1 138 1 | 120 | 120 | 0.05094 | 104.07 | Potential P4 Event - POI 588839_5 | Cumulative Impact | Upgrade the existing WLK X1 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27L | GEN-2023-134 | FROM->TO | 505590 WELEETK5 161 998044 WLK X1 138 1 | 120 | 120 | 0.05107 | 103.54 | Potential P4 Event - POI 588839_1 | Cumulative Impact | Upgrade the existing WLK X1 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27L | GEN-2023-134 | FROM->TO | 505590 WELEETK5 161 998044 WLK X1 138 1 | 120 | 120 | 0.06057 | 106.09 | 301551 4CHECOTA 138 505592 WELEETK4 138 1 | Cumulative Impact | Upgrade the existing WLK X1 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27L | GEN-2023-134 | FROM->TO | 505592 WELEETK4 138 998044 WLK X1 138 1 | 120 | 120 | 0.0507 | 101.73 | P42:345:OKGE:SB_FTTH7386:::: | Cumulative Impact | Upgrade the existing WLK X1 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27L | GEN-2023-134 | FROM->TO | 505592 WELEETK4 138 998044 WLK X1 138 1 | 120 | 120 | 0.05074 | 101.81 | P12:345:OKGE:BKRBKR295:::: | Cumulative Impact | Upgrade the existing WLK X1 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27L | GEN-2023-134 | FROM->TO | 505592 WELEETK4 138 998044 WLK X1 138 1 | 120 | 120 | 0.05074 | 101.81 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1 | Cumulative Impact | Upgrade the existing WLK X1 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27L | GEN-2023-134 | FROM->TO | 505592 WELEETK4 138 998044 WLK X1 138 1 | 120 | 120 | 0.05074 | 101.81 | P41:345:OKGE:SB_MUGE7385:::: | Cumulative Impact | Upgrade the existing WLK X1 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27L | GEN-2023-134 | FROM->TO | 505592 WELEETK4 138 998044 WLK X1 138 1 | 120 | 120 | 0.05094 | 103.69 | Potential P4 Event - POI 588839_5 | Cumulative Impact | Upgrade the existing WLK X1 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27L | GEN-2023-134 | FROM->TO | 505592 WELEETK4 138 998044 WLK X1 138 1 | 120 | 120 | 0.05107 | 103.13 | Potential P4 Event - POI 588839_1 | Cumulative Impact | Upgrade the existing WLK X1 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27L | GEN-2023-134 | FROM->TO | 505592 WELEETK4 138 998044 WLK X1 138 1 | 120 | 120 | 0.06057 | 105.85 | 301551 4CHECOTA 138 505592 WELEETK4 138 1 | Cumulative Impact | Upgrade the existing WLK X1 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27L | GEN-2023-134 | FROM->TO | 515077 FIXICO 2 69.0 997806 FIXICO4 69.0 4 | 62 | 67 | 0.20654 | 101.72 | 510902 WELETK4 138 774660 G23-134-TAP 138 1 | Cumulative Impact | Upgrade the existing FIXICO4 138/69 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27L | GEN-2023-134 | FROM->TO | 515078 FIXICO 4 138 997806 FIXICO4 69.0 4 | 62 | 67 | 0.20654 | 100.46 | 510902 WELETK4 138 774660 G23-134-TAP 138 1 | Cumulative Impact | Upgrade the existing FIXICO4 138/69 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-009 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.17173 | 109.58 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-009 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.17173 | 109.58 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-009 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.17173 | 109.58 | Potential P4 Event - POI 508359_5 | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-009 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.49353 | 105.14 | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-009 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.49353 | 105.14 | 521157 HUGO 7 345 3WXFMR HUGO 1 1 | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.2202 | 116.62 | P12:161:AEPW-EMDE:FLINTCR5:739952::: | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.22345 | 107.52 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.22345 | 107.55 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23684 | 107.8 | Potential P4 Event - POI 509745_2 | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23684 | 108.77 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23704 | 107.34 | Potential P4 Event - POI 509745_0 | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23704 | 107.68 | Potential P4 Event - POI 509745_1 | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23907 | 100.24 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23909 | 101.06 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23923 | 101.45 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.2396 | 112.16 | 512650 GRDA1 7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.2396 | 117.09 | Potential P4 Event - POI 774740_1 | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.2396 | 117.24 | Potential P4 Event - POI 774740_0 | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.2396 | 117.24 | Potential P4 Event - POI 774740_2 | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.2396 | 120.46 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23964 | 112.06 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23964 | 112.06 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23965 | 111.83 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 131 | 151 | 0.27994 | 104 | P13:69-138:AEPW:PRY-JCT2:::: | Cumulative Impact | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.2202 | 111.68 | P12:161:AEPW-EMDE:FLINTCR5:739952::: | Cumulative Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.22345 | 102.63 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.22345 | 102.64 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23684 | 103.01 | Potential P4 Event - POI 509745_2 | Cumulative Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23684 | 103.98 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23704 | 102.56 | Potential P4 Event - POI 509745_0 | Cumulative Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23704 | 102.89 | Potential P4 Event - POI 509745_1 | Cumulative Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.2396 | 107.33 | 512650 GRDA1 7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.2396 | 112.2 | Potential P4 Event - POI 774740_1 | Cumulative Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.2396 | 112.33 | Potential P4 Event - POI 774740_0 | Cumulative Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.2396 | 112.33 | Potential P4 Event - POI 774740_2 | Cumulative Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.2396 | 115.5 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23964 | 107.14 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | Cumulative Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23964 | 107.14 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 510421 JAY 4 138 1 | 131 | 151 | 0.23965 | 106.94 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing GROVE 4 to JAY 4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.18011 | 116.15 | P12:161:AEPW-EMDE:FLINTCR5:739952::: | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.18436 | 102.77 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.18436 | 102.89 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20242 | 101.85 | Potential P4 Event - POI 509745_2 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20242 | 102.77 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20259 | 101.36 | Potential P4 Event - POI 509745_0 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20259 | 101.74 | Potential P4 Event - POI 509745_1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.2055 | 107.33 | 512650 GRDA1 7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.2055 | 112.44 | Potential P4 Event - POI 774740_0 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.2055 | 112.45 | Potential P4 Event - POI 774740_2 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.2055 | 112.71 | Potential P4 Event - POI 774740_1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.2055 | 115.54 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20558 | 106.38 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20558 | 106.38 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20558 | 107.01 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.18011 | 117.1 | P12:161:AEPW-EMDE:FLINTCR5:739952::: | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.18436 | 103.36 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.18436 | 103.52 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20242 | 103.09 | Potential P4 Event - POI 509745_2 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20242 | 104.01 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20259 | 102.58 | Potential P4 Event - POI 509745_0 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20259 | 102.97 | Potential P4 Event - POI 509745_1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.2055 | 108.56 | 512650 GRDA1 7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.2055 | 113.64 | Potential P4 Event - POI 774740_0 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.2055 | 113.65 | Potential P4 Event - POI 774740_2 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.2055 | 113.99 | Potential P4 Event - POI 774740_1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.2055 | 116.75 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20558 | 107.21 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20558 | 107.21 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20558 | 108 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-027 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.06497 | 101.13 | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | 335 | 335 | 1 | 111.9 | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | Cumulative Impact | DRYGULCH5 to G23-028-TAP 161 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13171 | 148.6 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13171 | 148.75 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13263 | 148.32 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13263 | 149.33 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13385 | 144.73 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1339 | 144.43 | 547498 STL439 5 161 547657 S3G439 1 18.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13402 | 143.87 | P23:345:AEPW:NES CB 3417B NBTB:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13402 | 143.87 | P41:345:AEPW:NES CB 3417B NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13409 | 143.45 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13409 | 143.55 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13409 | 151.45 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13419 | 144.97 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13419 | 144.98 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13421 | 142.31 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13421 | 154.76 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13424 | 142.88 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13424 | 142.88 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13425 | 144.14 | P23:345:WERE:WICH-345-116:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13425 | 146.55 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13426 | 142.61 | P12:EHV:EES::7STFRAN!:7GOBKNOB%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13427 | 141.36 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13427 | 141.55 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13427 | 143.35 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13427 | 144.44 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13428 | 141.39 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13428 | 141.63 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13428 | 141.72 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13428 | 141.72 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13428 | 141.94 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13428 | 143.68 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13428 | 144.5 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13428 | 145.53 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13428 | 147.16 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13428 | 147.16 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13429 | 141.61 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13429 | 141.92 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13429 | 142.57 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13429 | 143.18 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13429 | 143.71 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 141.38 | 659336 TANDE___-BE3 345 659479 TRADEWND-UA3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 141.43 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 141.43 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 141.49 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 141.84 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 141.9 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 141.92 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 141.94 | 772981 GEN-2023-050 345 772982 G23-050XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 141.94 | 772981 GEN-2023-050 345 772985 G23-050XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 141.96 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 142.01 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 142.06 | GEN-2023-075_POI_773480_Generator_outage | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 142.2 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 142.25 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 142.3 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 142.39 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 142.39 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 142.51 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 142.64 | P23:345:MEC:LOUISA 954 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 142.74 | GEN-2023-050_POI_532793_Generator_outage | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 142.75 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 142.76 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 142.77 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 142.77 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 142.78 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 142.78 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 142.86 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 142.88 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 142.94 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 143.01 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 143.07 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 143.07 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 143.19 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 143.19 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 143.19 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 143.25 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 143.36 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 143.37 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 143.38 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 143.57 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 143.65 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 143.88 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 143.95 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 144.26 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 144.41 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 144.75 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 144.85 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 145.17 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 145.22 | 764300 GEN-2020-079 161 764310 G20-079-TAP 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 145.22 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 145.22 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1343 | 148.44 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13431 | 141.63 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13431 | 141.78 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13431 | 142.32 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13431 | 143.47 | 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13431 | 143.7 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13431 | 143.71 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13431 | 144.81 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13431 | 145.31 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13432 | 142.27 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13432 | 142.3 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13432 | 142.36 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13432 | 143.6 | P12:500-161:EES-EAI:M:NEW_MAD:PORTGV:WMPEHV:8BHAMSTE:HATI_S:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13432 | 143.61 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13432 | 143.62 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13432 | 144.05 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13432 | 145.91 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13432 | 146.77 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13434 | 144.08 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13439 | 142.63 | 506952 CENTRTN5 161 506980 SHIPERD5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1344 | 143.37 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13441 | 145.94 | P12:345:OKGE:BKRBKR400:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13446 | 146.57 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13448 | 150.38 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13448 | 151.14 | P42:345:OKGE:SB_OPKY7319:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13448 | 151.15 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13448 | 153.7 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13448 | 155.29 | Potential P4 Event - POI 560053_1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13448 | 155.31 | Potential P4 Event - POI 560053_2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13448 | 155.34 | Potential P4 Event - POI 560053_0 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13448 | 161.31 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13458 | 159.83 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13458 | 162.09 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13464 | 162.17 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13464 | 162.17 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13465 | 148.47 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13471 | 157.82 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13471 | 161.69 | Potential P4 Event - POI 773480_2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13471 | 161.72 | Potential P4 Event - POI 773480_0 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13471 | 161.77 | Potential P4 Event - POI 773480_1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13471 | 165.14 | Potential P4 Event - POI 532793_13 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13471 | 165.15 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13471 | 165.15 | Potential P4 Event - POI 532793_16 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13471 | 167.53 | Potential P4 Event - POI 532793_18 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1348 | 142.91 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13494 | 144.28 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13494 | 145.47 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13494 | 147.34 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13517 | 144.15 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13528 | 149.71 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13637 | 143.21 | 547579 COM381T2 69.0 547590 QUA377 2 69.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13637 | 143.75 | 547579 COM381T2 69.0 547583 FRL363 2 69.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13667 | 154.76 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13728 | 157.69 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13731 | 151.3 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.13811 | 163.38 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.14163 | 163.87 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.14223 | 148.2 | 512632 AFTON 5 161 3WXFMR AFTAUTO1 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.14587 | 148.24 | 512654 PENSA 5 161 3WXFMR PENAUTO1 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.30684 | 163.89 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13203 | 112.88 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13203 | 113.04 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13382 | 109.85 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13382 | 110.79 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13428 | 107.37 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13463 | 108.21 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13469 | 107.9 | 547498 STL439 5 161 547657 S3G439 1 18.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13483 | 107.64 | P23:345:AEPW:NES CB 3417B NBTB:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13483 | 107.64 | P41:345:AEPW:NES CB 3417B NBTB+FAULT:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13498 | 106.27 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13498 | 106.29 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13502 | 123.77 | 510417 VINTAJC4 138 547486 HOC404 4 138 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13502 | 123.77 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13505 | 105.76 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13506 | 107.51 | 512631 MIAMI 5 161 3WXFMR MIAAUTO2 2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13507 | 107.31 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13507 | 107.32 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13509 | 106.16 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13509 | 106.17 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1351 | 107.58 | P23:345:WERE:WICH-345-116:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1351 | 110.49 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13512 | 105.85 | P12:EHV:EES::7STFRAN!:7GOBKNOB%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13513 | 104.78 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13513 | 104.99 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13513 | 105.12 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13513 | 107.79 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13513 | 111.09 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13513 | 111.09 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13514 | 104.81 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13514 | 105.17 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13514 | 105.17 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13514 | 105.3 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13514 | 106.36 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13514 | 108.16 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13514 | 108.78 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13515 | 105 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13515 | 105.25 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13515 | 105.99 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13515 | 106.53 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13515 | 106.81 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13515 | 107.07 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 104.8 | 659336 TANDE___-BE3 345 659479 TRADEWND-UA3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 104.86 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 104.86 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 104.92 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 105.22 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 105.27 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 105.32 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 105.39 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 105.47 | 772981 GEN-2023-050 345 772982 G23-050XFMR1 34.5 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 105.47 | 772981 GEN-2023-050 345 772985 G23-050XFMR2 34.5 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 105.55 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 105.62 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 105.66 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 105.75 | GEN-2023-075_POI_773480_Generator_outage | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 105.84 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 105.84 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 105.87 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 105.93 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 105.99 | P23:345:MEC:LOUISA 954 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 106.17 | P23:345:XEL:8N8 MNN | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 106.18 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 106.18 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 106.19 | P23:345:XEL:8N22 SHC | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 106.2 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 106.2 | P23:345:XEL:8N17 SHC | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 106.24 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 106.29 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 106.38 | GEN-2023-050_POI_532793_Generator_outage | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 106.38 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 106.38 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 106.46 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 106.63 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 106.67 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 106.67 | P23:345:MEC:CBEC 908 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 106.75 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 106.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 106.86 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 106.88 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 106.89 | P23:345:MEC:CBEC 905 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 107.15 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 107.21 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 107.33 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 107.42 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 107.49 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 107.94 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 108.47 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 108.88 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 109 | 764300 GEN-2020-079 161 764310 G20-079-TAP 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 109 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13516 | 109 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13517 | 105.44 | P23:345:AMMO::MONTGOMERY:V43:: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13517 | 106.6 | 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13517 | 106.8 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13517 | 106.81 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13517 | 107.93 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13517 | 108.5 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13517 | 111.94 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13518 | 105.16 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13518 | 105.31 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13518 | 105.59 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13518 | 108.95 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13518 | 109.75 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13519 | 105.71 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13519 | 105.75 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13519 | 105.8 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13519 | 106.84 | P12:500-161:EES-EAI:M:NEW_MAD:PORTGV:WMPEHV:8BHAMSTE:HATI_S:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13519 | 106.86 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13519 | 106.93 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13519 | 107.32 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1352 | 107.33 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13524 | 105.68 | 506952 CENTRTN5 161 506980 SHIPERD5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13525 | 106.27 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13529 | 109.38 | P12:345:OKGE:BKRBKR400:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13536 | 114.06 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13536 | 115.05 | P42:345:OKGE:SB_OPKY7319:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13536 | 115.05 | P42:345:OKGE:SB_OPKY7388:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13536 | 115.06 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13536 | 117.39 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13536 | 119.46 | Potential P4 Event - POI 560053_1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13536 | 119.49 | Potential P4 Event - POI 560053_2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13536 | 119.5 | Potential P4 Event - POI 560053_0 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13536 | 124.91 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13548 | 124.63 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13548 | 126.92 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13556 | 126.99 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13556 | 126.99 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13559 | 112.5 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13565 | 122.41 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13565 | 126.67 | Potential P4 Event - POI 773480_0 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13565 | 126.67 | Potential P4 Event - POI 773480_2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13565 | 126.73 | Potential P4 Event - POI 773480_1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13565 | 129.88 | Potential P4 Event - POI 532793_13 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13565 | 129.91 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13565 | 129.91 | Potential P4 Event - POI 532793_16 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13565 | 132.47 | Potential P4 Event - POI 532793_18 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13567 | 106.25 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13571 | 107.06 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13571 | 108.31 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13571 | 109.32 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13606 | 111.63 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13723 | 110.84 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13773 | 117.58 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13799 | 118.68 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13825 | 114.22 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.14004 | 109.08 | 547579 COM381T2 69.0 547590 QUA377 2 69.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.14004 | 110.2 | 547579 COM381T2 69.0 547583 FRL363 2 69.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.14109 | 118.19 | 300852 2MIAETP 69.0 512630 MIAMI 2 69.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.14316 | 127.1 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.30429 | 125.42 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14523 | 165.14 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14523 | 166.18 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14533 | 160.71 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14533 | 160.87 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14718 | 155.85 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14745 | 156.89 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1475 | 156.59 | 547498 STL439 5 161 547657 S3G439 1 18.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14763 | 156 | P23:345:AEPW:NES CB 3417B NBTB:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14763 | 156 | P41:345:AEPW:NES CB 3417B NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14769 | 155.65 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14769 | 155.75 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1477 | 163.6 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14779 | 157.36 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14779 | 157.38 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14782 | 154.45 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14785 | 155.01 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14785 | 155.02 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14785 | 161.76 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14786 | 156.25 | P23:345:WERE:WICH-345-116:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14786 | 158.67 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14787 | 154.75 | P12:EHV:EES::7STFRAN!:7GOBKNOB%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14788 | 153.48 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14788 | 153.67 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14788 | 155.54 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14788 | 156.57 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14788 | 173.66 | Potential P4 Event - POI 532794_2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14789 | 153.51 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14789 | 153.75 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14789 | 153.84 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14789 | 153.84 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14789 | 154.06 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14789 | 155.87 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14789 | 156.63 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14789 | 157.66 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14789 | 159.29 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14789 | 159.29 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1479 | 153.73 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1479 | 154.04 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1479 | 154.7 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1479 | 155.3 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1479 | 155.84 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 153.5 | 659336 TANDE___-BE3 345 659479 TRADEWND-UA3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 153.55 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 153.55 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 153.61 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 153.96 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 154.03 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 154.04 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 154.06 | 772981 GEN-2023-050 345 772982 G23-050XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 154.08 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 154.14 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 154.35 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 154.38 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 154.44 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 154.53 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 154.53 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 154.65 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 154.78 | P23:345:MEC:LOUISA 954 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 154.81 | 771661 GEN-2022-234 138 771662 G22-234XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 154.81 | GEN-2022-234_POI_771660_Generator_outage | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 154.85 | GEN-2023-050_POI_532793_Generator_outage | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 154.89 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 154.9 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 154.91 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 154.91 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 154.92 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 154.92 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 155.01 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 155.02 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 155.13 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 155.15 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 155.22 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 155.22 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 155.34 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 155.34 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 155.34 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 155.39 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 155.5 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 155.52 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 155.53 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 155.7 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 155.8 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 156.03 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 156.1 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 156.44 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 156.59 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 156.89 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 156.97 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 157.31 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 157.34 | 764300 GEN-2020-079 161 764310 G20-079-TAP 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 157.34 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 157.34 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 160.53 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14792 | 153.75 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14792 | 153.9 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14792 | 154.46 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14792 | 155.62 | 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14792 | 155.83 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14792 | 155.85 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14792 | 156.94 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14792 | 157.5 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14793 | 154.37 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14793 | 154.4 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14793 | 154.46 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14793 | 155.77 | P12:500-161:EES-EAI:M:NEW_MAD:PORTGV:WMPEHV:8BHAMSTE:HATI_S:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14793 | 155.78 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14793 | 155.78 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14793 | 158.12 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14793 | 159.01 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14794 | 156.22 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14795 | 156.25 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14799 | 154.14 | 547561 NOL443 2 69.0 547566 AND322 2 69.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14799 | 154.52 | 547561 NOL443 2 69.0 547610 NOL435 2 69.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14801 | 154.84 | 506952 CENTRTN5 161 506980 SHIPERD5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14802 | 155.59 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14802 | 158.06 | P12:345:OKGE:BKRBKR400:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14806 | 173.72 | Potential P4 Event - POI 532794_5 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14808 | 159.12 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14808 | 162.45 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14808 | 163.22 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14808 | 163.22 | P42:345:OKGE:SB_OPKY7319:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14808 | 165.77 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14808 | 167.37 | Potential P4 Event - POI 560053_1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14808 | 167.37 | Potential P4 Event - POI 560053_2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14808 | 167.42 | Potential P4 Event - POI 560053_0 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14808 | 173.41 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14818 | 171.88 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14818 | 174.16 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14823 | 160.24 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14824 | 174.23 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14824 | 174.23 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14832 | 169.72 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14832 | 173.66 | Potential P4 Event - POI 773480_1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14832 | 177.02 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14832 | 177.02 | Potential P4 Event - POI 532793_13 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14832 | 177.02 | Potential P4 Event - POI 532793_16 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14832 | 179.41 | Potential P4 Event - POI 532793_18 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14844 | 155.14 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14857 | 156.51 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14857 | 157.74 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14857 | 159.7 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14871 | 156.04 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14889 | 161.89 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.15034 | 167.29 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.15106 | 170.76 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.15113 | 164.12 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.15196 | 176.91 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.15551 | 176.85 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.17 | 167.27 | 512654 PENSA 5 161 3WXFMR PENAUTO1 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.34195 | 178.83 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512633 AFTON 2 69.0 512708 FAIRTAP2 69.0 1 | 72 | 72 | 0.05147 | 196.52 | P21:161:GRDA:MIAMI5-AFTON5:::HV: | Cumulative Impact | AFTON2 to FAIRTAP2 69 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14523 | 169.99 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14523 | 171.04 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14533 | 165.57 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14533 | 165.72 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14718 | 160.7 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14745 | 161.74 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1475 | 161.45 | 547498 STL439 5 161 547657 S3G439 1 18.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14763 | 160.84 | P23:345:AEPW:NES CB 3417B NBTB:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14763 | 160.84 | P41:345:AEPW:NES CB 3417B NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14769 | 160.5 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14769 | 160.6 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1477 | 168.49 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14779 | 162.22 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14779 | 162.23 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14782 | 159.29 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14785 | 159.86 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14785 | 159.86 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14785 | 166.61 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14786 | 161.1 | P23:345:WERE:WICH-345-116:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14786 | 163.53 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14787 | 159.6 | P12:EHV:EES::7STFRAN!:7GOBKNOB%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14788 | 158.32 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14788 | 158.51 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14788 | 160.39 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14788 | 161.42 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14788 | 178.6 | Potential P4 Event - POI 532794_2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14789 | 158.35 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14789 | 158.59 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14789 | 158.68 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14789 | 158.68 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14789 | 158.9 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14789 | 160.71 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14789 | 161.49 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14789 | 162.52 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14789 | 164.16 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14789 | 164.16 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1479 | 158.57 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1479 | 158.88 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1479 | 159.55 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1479 | 160.15 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1479 | 160.69 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 158.34 | 659336 TANDE___-BE3 345 659479 TRADEWND-UA3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 158.39 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 158.39 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 158.44 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 158.8 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 158.87 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 158.88 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 158.89 | 772981 GEN-2023-050 345 772985 G23-050XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 158.93 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 158.98 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 159.19 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 159.23 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 159.28 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 159.37 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 159.37 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 159.49 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 159.62 | P23:345:MEC:LOUISA 954 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 159.65 | 771661 GEN-2022-234 138 771662 G22-234XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 159.65 | GEN-2022-234_POI_771660_Generator_outage | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 159.69 | GEN-2023-050_POI_532793_Generator_outage | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 159.74 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 159.75 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 159.76 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 159.76 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 159.76 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 159.77 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 159.85 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 159.87 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 159.98 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 160 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 160.07 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 160.07 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 160.18 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 160.18 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 160.19 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 160.24 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 160.35 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 160.37 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 160.38 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 160.55 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 160.65 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 160.88 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 160.96 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 161.3 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 161.46 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 161.74 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 161.82 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 162.17 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 162.2 | 764300 GEN-2020-079 161 764310 G20-079-TAP 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 162.2 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 162.2 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14791 | 165.4 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14792 | 158.58 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14792 | 158.74 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14792 | 159.31 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14792 | 160.48 | 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14792 | 160.69 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14792 | 160.7 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14792 | 161.8 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14792 | 162.37 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14793 | 159.21 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14793 | 159.25 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14793 | 159.3 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14793 | 160.62 | P12:500-161:EES-EAI:M:NEW_MAD:PORTGV:WMPEHV:8BHAMSTE:HATI_S:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14793 | 160.63 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14793 | 160.63 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14793 | 162.98 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14793 | 163.88 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14794 | 161.07 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14795 | 161.1 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14799 | 158.98 | 547561 NOL443 2 69.0 547566 AND322 2 69.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14799 | 159.36 | 547561 NOL443 2 69.0 547610 NOL435 2 69.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14801 | 159.68 | 506952 CENTRTN5 161 506980 SHIPERD5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14802 | 160.43 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14802 | 162.91 | P12:345:OKGE:BKRBKR400:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14806 | 178.66 | Potential P4 Event - POI 532794_5 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14808 | 164.01 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14808 | 167.32 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14808 | 168.09 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14808 | 168.09 | P42:345:OKGE:SB_OPKY7319:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14808 | 170.66 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14808 | 172.26 | Potential P4 Event - POI 560053_1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14808 | 172.27 | Potential P4 Event - POI 560053_2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14808 | 172.31 | Potential P4 Event - POI 560053_0 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14808 | 178.35 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14818 | 176.76 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14818 | 179.05 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14823 | 165.1 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14824 | 179.13 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14824 | 179.13 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14832 | 174.6 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14832 | 178.57 | Potential P4 Event - POI 773480_1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14832 | 181.94 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14832 | 181.94 | Potential P4 Event - POI 532793_16 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14832 | 181.95 | Potential P4 Event - POI 532793_13 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14832 | 184.34 | Potential P4 Event - POI 532793_18 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14844 | 159.99 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14857 | 161.36 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14857 | 162.59 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14857 | 164.56 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14871 | 160.88 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.14889 | 166.75 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.15034 | 172.19 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.15106 | 175.66 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.15113 | 169 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.15196 | 181.84 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.15551 | 181.75 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.17 | 172.12 | 512654 PENSA 5 161 3WXFMR PENAUTO1 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.34195 | 183.73 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 113.31 | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 133.85 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-028 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.06652 | 101.13 | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-038 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.06198 | 109.58 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-038 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.06198 | 109.58 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-038 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.06198 | 109.58 | Potential P4 Event - POI 508359_5 | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-038 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.0641 | 105.14 | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-038 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.0641 | 105.14 | 521157 HUGO 7 345 3WXFMR HUGO 1 1 | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | 335 | 335 | 1 | 111.9 | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | Cumulative Impact | DRYGULCH5 to G23-028-TAP 161 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16199 | 148.6 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16199 | 148.75 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16288 | 148.32 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16288 | 149.33 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16444 | 154.76 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16462 | 144.73 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16467 | 144.43 | 547498 STL439 5 161 547657 S3G439 1 18.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16473 | 144.97 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16473 | 144.98 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16478 | 143.87 | P23:345:AEPW:NES CB 3417B NBTB:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16478 | 143.87 | P41:345:AEPW:NES CB 3417B NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16485 | 143.45 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16485 | 143.55 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16485 | 151.45 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16498 | 142.31 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16501 | 142.88 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16501 | 142.88 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16502 | 143.35 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16502 | 144.14 | P23:345:WERE:WICH-345-116:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16502 | 146.55 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16504 | 142.61 | P12:EHV:EES::7STFRAN!:7GOBKNOB%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16505 | 141.36 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16505 | 141.55 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16505 | 143.68 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16505 | 144.44 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16505 | 147.16 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16505 | 147.16 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16506 | 141.39 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16506 | 141.61 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16506 | 141.63 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16506 | 141.72 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16506 | 141.72 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16506 | 141.92 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16506 | 141.94 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16506 | 144.5 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16506 | 145.53 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 141.38 | 659336 TANDE___-BE3 345 659479 TRADEWND-UA3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 141.43 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 141.43 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 141.49 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 141.84 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 141.9 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 141.92 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 141.94 | 772981 GEN-2023-050 345 772982 G23-050XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 141.94 | 772981 GEN-2023-050 345 772985 G23-050XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 141.96 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 142.06 | GEN-2023-075_POI_773480_Generator_outage | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 142.2 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 142.25 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 142.39 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 142.39 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 142.51 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 142.57 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 142.64 | P23:345:MEC:LOUISA 954 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 142.74 | GEN-2023-050_POI_532793_Generator_outage | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 142.75 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 142.76 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 142.77 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 142.77 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 142.78 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 142.78 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 142.86 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 142.88 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 142.94 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 143.01 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 143.18 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 143.19 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 143.19 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 143.19 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 143.25 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 143.36 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 143.37 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 143.38 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 143.65 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 143.71 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 143.88 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 143.95 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 144.26 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 144.41 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 144.85 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 145.17 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 145.22 | 764300 GEN-2020-079 161 764310 G20-079-TAP 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 145.22 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 145.22 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16507 | 148.44 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16508 | 141.78 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16508 | 142.01 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16508 | 142.3 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16508 | 143.07 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16508 | 143.07 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16508 | 143.47 | 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16508 | 143.57 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16508 | 143.7 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16508 | 143.71 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16508 | 144.75 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16508 | 144.81 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16509 | 141.63 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16509 | 142.32 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16509 | 145.31 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16509 | 145.91 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16509 | 146.77 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1651 | 142.27 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1651 | 142.3 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1651 | 142.36 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1651 | 143.6 | P12:500-161:EES-EAI:M:NEW_MAD:PORTGV:WMPEHV:8BHAMSTE:HATI_S:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1651 | 143.61 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1651 | 143.62 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.1651 | 144.05 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16511 | 144.08 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16511 | 159.83 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16511 | 162.09 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16516 | 142.63 | 506952 CENTRTN5 161 506980 SHIPERD5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16517 | 143.37 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16517 | 162.17 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16517 | 162.17 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16518 | 145.94 | P12:345:OKGE:BKRBKR400:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16522 | 146.57 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16522 | 150.38 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16522 | 151.14 | P42:345:OKGE:SB_OPKY7319:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16522 | 151.15 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16522 | 153.7 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16522 | 155.29 | Potential P4 Event - POI 560053_1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16522 | 155.31 | Potential P4 Event - POI 560053_2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16522 | 155.34 | Potential P4 Event - POI 560053_0 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16522 | 161.31 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16528 | 157.82 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16528 | 161.69 | Potential P4 Event - POI 773480_2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16528 | 161.72 | Potential P4 Event - POI 773480_0 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16528 | 161.77 | Potential P4 Event - POI 773480_1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16528 | 165.14 | Potential P4 Event - POI 532793_13 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16528 | 165.15 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16528 | 165.15 | Potential P4 Event - POI 532793_16 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16528 | 167.53 | Potential P4 Event - POI 532793_18 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16535 | 148.47 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16554 | 142.91 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16559 | 144.28 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16559 | 145.47 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16559 | 147.34 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16574 | 149.71 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16586 | 144.15 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16731 | 154.76 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16755 | 143.21 | 547579 COM381T2 69.0 547590 QUA377 2 69.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16755 | 143.75 | 547579 COM381T2 69.0 547583 FRL363 2 69.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16776 | 157.69 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16788 | 151.3 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.16843 | 163.38 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.17189 | 163.87 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.17525 | 148.2 | 512632 AFTON 5 161 3WXFMR AFTAUTO1 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.17984 | 148.24 | 512654 PENSA 5 161 3WXFMR PENAUTO1 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.30684 | 163.89 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16159 | 112.88 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16159 | 113.04 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16357 | 109.85 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16357 | 110.79 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16428 | 107.37 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16435 | 123.77 | 510417 VINTAJC4 138 547486 HOC404 4 138 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16435 | 123.77 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1648 | 108.21 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16486 | 107.9 | 547498 STL439 5 161 547657 S3G439 1 18.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16497 | 107.64 | P23:345:AEPW:NES CB 3417B NBTB:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16497 | 107.64 | P41:345:AEPW:NES CB 3417B NBTB+FAULT:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16505 | 107.31 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16505 | 107.32 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16514 | 106.27 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16514 | 106.29 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16522 | 105.76 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16526 | 106.16 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16526 | 106.17 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16526 | 107.58 | P23:345:WERE:WICH-345-116:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16527 | 110.49 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16528 | 106.36 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16529 | 105.85 | P12:EHV:EES::7STFRAN!:7GOBKNOB%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1653 | 104.78 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1653 | 104.99 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1653 | 105.12 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1653 | 107.51 | 512631 MIAMI 5 161 3WXFMR MIAAUTO2 2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1653 | 107.79 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1653 | 108.78 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1653 | 111.09 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1653 | 111.09 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16531 | 104.81 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16531 | 105 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16531 | 105.17 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16531 | 105.17 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16531 | 105.25 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16531 | 105.3 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16531 | 106.81 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16531 | 108.16 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 104.8 | 659336 TANDE___-BE3 345 659479 TRADEWND-UA3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 104.86 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 104.86 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 104.92 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 105.22 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 105.27 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 105.39 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 105.47 | 772981 GEN-2023-050 345 772982 G23-050XFMR1 34.5 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 105.47 | 772981 GEN-2023-050 345 772985 G23-050XFMR2 34.5 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 105.55 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 105.66 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 105.75 | GEN-2023-075_POI_773480_Generator_outage | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 105.84 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 105.84 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 105.87 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 105.93 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 105.99 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 106.17 | P23:345:XEL:8N8 MNN | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 106.18 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 106.18 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 106.19 | P23:345:XEL:8N22 SHC | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 106.2 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 106.2 | P23:345:XEL:8N17 SHC | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 106.24 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 106.29 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 106.38 | GEN-2023-050_POI_532793_Generator_outage | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 106.46 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 106.53 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 106.63 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 106.67 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 106.67 | P23:345:MEC:CBEC 908 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 106.75 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 106.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 106.88 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 107.07 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 107.15 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 107.21 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 107.33 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 107.42 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 107.49 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 108.88 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 109 | 764300 GEN-2020-079 161 764310 G20-079-TAP 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 109 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 109 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16532 | 111.94 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16533 | 105.32 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16533 | 105.62 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16533 | 105.99 | P23:345:MEC:LOUISA 954 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16533 | 106.38 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16533 | 106.38 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16533 | 106.6 | 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16533 | 106.8 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16533 | 106.81 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16533 | 106.86 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16533 | 106.89 | P23:345:MEC:CBEC 905 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16533 | 107.93 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16533 | 107.94 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16533 | 108.47 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16534 | 105.31 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16534 | 105.44 | P23:345:AMMO::MONTGOMERY:V43:: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16534 | 105.59 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16534 | 108.5 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16534 | 108.95 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16534 | 109.75 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16535 | 105.16 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16535 | 105.71 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16535 | 105.75 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16535 | 105.8 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16535 | 106.84 | P12:500-161:EES-EAI:M:NEW_MAD:PORTGV:WMPEHV:8BHAMSTE:HATI_S:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16535 | 106.86 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16535 | 106.93 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16535 | 107.32 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16536 | 107.33 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16537 | 124.63 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16537 | 126.92 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1654 | 105.68 | 506952 CENTRTN5 161 506980 SHIPERD5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16541 | 106.27 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16544 | 109.38 | P12:345:OKGE:BKRBKR400:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16544 | 126.99 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16544 | 126.99 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16549 | 114.06 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16549 | 115.05 | P42:345:OKGE:SB_OPKY7319:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16549 | 115.05 | P42:345:OKGE:SB_OPKY7388:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16549 | 115.06 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16549 | 117.39 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16549 | 119.46 | Potential P4 Event - POI 560053_1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16549 | 119.49 | Potential P4 Event - POI 560053_2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16549 | 119.5 | Potential P4 Event - POI 560053_0 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16549 | 124.91 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16557 | 122.41 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16557 | 126.67 | Potential P4 Event - POI 773480_0 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16557 | 126.67 | Potential P4 Event - POI 773480_2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16557 | 126.73 | Potential P4 Event - POI 773480_1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16557 | 129.88 | Potential P4 Event - POI 532793_13 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16557 | 129.91 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16557 | 129.91 | Potential P4 Event - POI 532793_16 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16557 | 132.47 | Potential P4 Event - POI 532793_18 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16566 | 112.5 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16577 | 107.06 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16577 | 108.31 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16577 | 109.32 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16581 | 106.25 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16593 | 111.63 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16719 | 110.84 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16775 | 117.58 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16787 | 118.68 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1682 | 114.22 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.17116 | 109.08 | 547579 COM381T2 69.0 547590 QUA377 2 69.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.17116 | 110.2 | 547579 COM381T2 69.0 547583 FRL363 2 69.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.17273 | 118.19 | 300852 2MIAETP 69.0 512630 MIAMI 2 69.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.17276 | 127.1 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.30429 | 125.42 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.17899 | 165.14 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.17899 | 166.18 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.17943 | 160.71 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.17943 | 160.87 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18165 | 155.85 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18207 | 156.89 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18212 | 156.59 | 547498 STL439 5 161 547657 S3G439 1 18.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18213 | 161.76 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18215 | 157.36 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18215 | 157.38 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18223 | 156 | P23:345:AEPW:NES CB 3417B NBTB:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18223 | 156 | P41:345:AEPW:NES CB 3417B NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18229 | 155.65 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18229 | 155.75 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1823 | 163.6 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18243 | 154.45 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18245 | 173.66 | Potential P4 Event - POI 532794_2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18246 | 155.01 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18246 | 155.02 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18247 | 155.54 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18247 | 156.25 | P23:345:WERE:WICH-345-116:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18247 | 158.67 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18248 | 154.75 | P12:EHV:EES::7STFRAN!:7GOBKNOB%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18249 | 153.67 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18249 | 155.87 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18249 | 156.57 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1825 | 153.48 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1825 | 153.51 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1825 | 153.75 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1825 | 154.06 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1825 | 156.63 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1825 | 157.66 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1825 | 159.29 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1825 | 159.29 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18251 | 153.73 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18251 | 153.84 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18251 | 153.84 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18251 | 154.04 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18251 | 154.7 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18251 | 155.3 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18251 | 155.84 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18251 | 160.53 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 153.5 | 659336 TANDE___-BE3 345 659479 TRADEWND-UA3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 153.55 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 153.55 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 153.61 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 153.96 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 154.03 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 154.04 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 154.06 | 772981 GEN-2023-050 345 772982 G23-050XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 154.08 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 154.14 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 154.35 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 154.38 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 154.44 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 154.53 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 154.53 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 154.65 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 154.78 | P23:345:MEC:LOUISA 954 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 154.81 | 771661 GEN-2022-234 138 771662 G22-234XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 154.81 | GEN-2022-234_POI_771660_Generator_outage | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 154.85 | GEN-2023-050_POI_532793_Generator_outage | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 154.89 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 154.9 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 154.91 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 154.91 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 154.92 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 154.92 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 155.01 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 155.02 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 155.13 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 155.15 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 155.22 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 155.22 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 155.34 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 155.34 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 155.34 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 155.39 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 155.5 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 155.52 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 155.53 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 155.7 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 155.8 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 156.03 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 156.1 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 156.44 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 156.59 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 156.89 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 156.97 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 157.31 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 157.34 | 764300 GEN-2020-079 161 764310 G20-079-TAP 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 157.34 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 157.34 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18253 | 153.75 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18253 | 153.9 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18253 | 154.46 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18253 | 155.62 | 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18253 | 155.83 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18253 | 155.85 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18253 | 156.94 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18253 | 157.5 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18253 | 158.12 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18254 | 154.37 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18254 | 154.4 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18254 | 154.46 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18254 | 155.77 | P12:500-161:EES-EAI:M:NEW_MAD:PORTGV:WMPEHV:8BHAMSTE:HATI_S:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18254 | 155.78 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18254 | 155.78 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18254 | 159.01 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18255 | 156.22 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18256 | 154.14 | 547561 NOL443 2 69.0 547566 AND322 2 69.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18256 | 154.52 | 547561 NOL443 2 69.0 547610 NOL435 2 69.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18256 | 156.25 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18256 | 171.88 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18256 | 174.16 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18261 | 154.84 | 506952 CENTRTN5 161 506980 SHIPERD5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18261 | 174.23 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18261 | 174.23 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18262 | 155.59 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18262 | 158.06 | P12:345:OKGE:BKRBKR400:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18264 | 173.72 | Potential P4 Event - POI 532794_5 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18266 | 162.45 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18266 | 163.22 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18266 | 163.22 | P42:345:OKGE:SB_OPKY7319:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18266 | 165.77 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18266 | 167.37 | Potential P4 Event - POI 560053_1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18266 | 167.37 | Potential P4 Event - POI 560053_2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18266 | 167.42 | Potential P4 Event - POI 560053_0 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18266 | 173.41 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18267 | 159.12 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18273 | 169.72 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18273 | 173.66 | Potential P4 Event - POI 773480_1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18273 | 177.02 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18273 | 177.02 | Potential P4 Event - POI 532793_13 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18273 | 177.02 | Potential P4 Event - POI 532793_16 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18273 | 179.41 | Potential P4 Event - POI 532793_18 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18277 | 160.24 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18302 | 155.14 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18305 | 156.51 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18305 | 157.74 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18305 | 159.7 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18319 | 161.89 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18325 | 156.04 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18482 | 167.29 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18535 | 170.76 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18551 | 164.12 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18609 | 176.91 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18959 | 176.85 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.21069 | 167.27 | 512654 PENSA 5 161 3WXFMR PENAUTO1 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.34195 | 178.83 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512633 AFTON 2 69.0 512708 FAIRTAP2 69.0 1 | 72 | 72 | 0.06231 | 196.52 | P21:161:GRDA:MIAMI5-AFTON5:::HV: | Cumulative Impact | AFTON2 to FAIRTAP2 69 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.17899 | 169.99 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.17899 | 171.04 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.17943 | 165.57 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.17943 | 165.72 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18165 | 160.7 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18207 | 161.74 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18212 | 161.45 | 547498 STL439 5 161 547657 S3G439 1 18.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18213 | 166.61 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18215 | 162.22 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18215 | 162.23 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18223 | 160.84 | P23:345:AEPW:NES CB 3417B NBTB:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18223 | 160.84 | P41:345:AEPW:NES CB 3417B NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18229 | 160.5 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18229 | 160.6 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1823 | 168.49 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18243 | 159.29 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18245 | 178.6 | Potential P4 Event - POI 532794_2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18246 | 159.86 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18246 | 159.86 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18247 | 160.39 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18247 | 161.1 | P23:345:WERE:WICH-345-116:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18247 | 163.53 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18248 | 159.6 | P12:EHV:EES::7STFRAN!:7GOBKNOB%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18249 | 158.51 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18249 | 160.71 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18249 | 161.42 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1825 | 158.32 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1825 | 158.35 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1825 | 158.59 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1825 | 158.9 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1825 | 161.49 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1825 | 162.52 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1825 | 164.16 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.1825 | 164.16 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18251 | 158.57 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18251 | 158.68 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18251 | 158.68 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18251 | 158.88 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18251 | 159.55 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18251 | 160.15 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18251 | 160.69 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18251 | 165.4 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 158.34 | 659336 TANDE___-BE3 345 659479 TRADEWND-UA3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 158.39 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 158.39 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 158.44 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 158.8 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 158.87 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 158.88 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 158.89 | 772981 GEN-2023-050 345 772985 G23-050XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 158.93 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 158.98 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 159.19 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 159.23 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 159.28 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 159.37 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 159.37 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 159.49 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 159.62 | P23:345:MEC:LOUISA 954 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 159.65 | 771661 GEN-2022-234 138 771662 G22-234XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 159.65 | GEN-2022-234_POI_771660_Generator_outage | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 159.69 | GEN-2023-050_POI_532793_Generator_outage | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 159.74 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 159.75 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 159.76 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 159.76 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 159.76 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 159.77 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 159.85 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 159.87 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 159.98 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 160 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 160.07 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 160.07 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 160.18 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 160.18 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 160.19 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 160.24 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 160.35 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 160.37 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 160.38 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 160.55 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 160.65 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 160.88 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 160.96 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 161.3 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 161.46 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 161.74 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 161.82 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 162.17 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 162.2 | 764300 GEN-2020-079 161 764310 G20-079-TAP 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 162.2 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18252 | 162.2 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18253 | 158.58 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18253 | 158.74 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18253 | 159.31 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18253 | 160.48 | 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18253 | 160.69 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18253 | 160.7 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18253 | 161.8 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18253 | 162.37 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18253 | 162.98 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18254 | 159.21 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18254 | 159.25 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18254 | 159.3 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18254 | 160.62 | P12:500-161:EES-EAI:M:NEW_MAD:PORTGV:WMPEHV:8BHAMSTE:HATI_S:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18254 | 160.63 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18254 | 160.63 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18254 | 163.88 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18255 | 161.07 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18256 | 158.98 | 547561 NOL443 2 69.0 547566 AND322 2 69.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18256 | 159.36 | 547561 NOL443 2 69.0 547610 NOL435 2 69.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18256 | 161.1 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18256 | 176.76 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18256 | 179.05 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18261 | 159.68 | 506952 CENTRTN5 161 506980 SHIPERD5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18261 | 179.13 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18261 | 179.13 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18262 | 160.43 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18262 | 162.91 | P12:345:OKGE:BKRBKR400:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18264 | 178.66 | Potential P4 Event - POI 532794_5 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18266 | 167.32 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18266 | 168.09 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18266 | 168.09 | P42:345:OKGE:SB_OPKY7319:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18266 | 170.66 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18266 | 172.26 | Potential P4 Event - POI 560053_1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18266 | 172.27 | Potential P4 Event - POI 560053_2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18266 | 172.31 | Potential P4 Event - POI 560053_0 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18266 | 178.35 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18267 | 164.01 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18273 | 174.6 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18273 | 178.57 | Potential P4 Event - POI 773480_1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18273 | 181.94 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18273 | 181.94 | Potential P4 Event - POI 532793_16 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18273 | 181.95 | Potential P4 Event - POI 532793_13 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18273 | 184.34 | Potential P4 Event - POI 532793_18 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18277 | 165.1 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18302 | 159.99 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18305 | 161.36 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18305 | 162.59 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18305 | 164.56 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18319 | 166.75 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18325 | 160.88 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18482 | 172.19 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18535 | 175.66 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18551 | 169 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18609 | 181.84 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.18959 | 181.75 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.21069 | 172.12 | 512654 PENSA 5 161 3WXFMR PENAUTO1 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.34195 | 183.73 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 113.31 | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 133.85 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-049 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.06692 | 101.13 | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.05967 | 148.6 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.05967 | 148.75 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06057 | 163.89 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06058 | 148.32 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06058 | 149.33 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06072 | 144.73 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06077 | 144.43 | 547498 STL439 5 161 547657 S3G439 1 18.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06096 | 143.87 | P23:345:AEPW:NES CB 3417B NBTB:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06096 | 143.87 | P41:345:AEPW:NES CB 3417B NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06098 | 143.45 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06098 | 143.55 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06099 | 151.45 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06108 | 142.31 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06112 | 142.88 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06112 | 142.88 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06113 | 146.55 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06114 | 142.61 | P12:EHV:EES::7STFRAN!:7GOBKNOB%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06114 | 144.14 | P23:345:WERE:WICH-345-116:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06115 | 141.36 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06115 | 141.39 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06115 | 141.55 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06115 | 141.63 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06115 | 144.44 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06115 | 144.5 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06115 | 147.16 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06115 | 147.16 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06116 | 141.61 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06116 | 141.72 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06116 | 141.72 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06116 | 141.92 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06116 | 141.94 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06116 | 142.57 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06116 | 145.53 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 141.38 | 659336 TANDE___-BE3 345 659479 TRADEWND-UA3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 141.43 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 141.43 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 141.49 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 141.84 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 141.9 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 141.92 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 141.94 | 772981 GEN-2023-050 345 772982 G23-050XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 141.94 | 772981 GEN-2023-050 345 772985 G23-050XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 141.96 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 142.01 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 142.06 | GEN-2023-075_POI_773480_Generator_outage | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 142.2 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 142.25 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 142.39 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 142.39 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 142.51 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 142.64 | P23:345:MEC:LOUISA 954 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 142.74 | GEN-2023-050_POI_532793_Generator_outage | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 142.75 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 142.76 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 142.77 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 142.77 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 142.78 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 142.78 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 142.86 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 142.88 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 142.94 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 143.01 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 143.18 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 143.19 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 143.19 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 143.19 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 143.25 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 143.36 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 143.37 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 143.38 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 143.65 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 143.71 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 143.88 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 143.95 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 144.26 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 144.41 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 144.85 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 145.22 | 764300 GEN-2020-079 161 764310 G20-079-TAP 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 145.22 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06117 | 145.22 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06118 | 141.63 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06118 | 141.78 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06118 | 142.3 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06118 | 143.07 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06118 | 143.07 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06118 | 143.47 | 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06118 | 143.57 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06118 | 143.68 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06118 | 143.7 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06118 | 143.71 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06118 | 144.75 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06118 | 144.81 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06118 | 145.17 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06119 | 142.32 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.0612 | 142.27 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.0612 | 142.3 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.0612 | 142.36 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.0612 | 143.35 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.0612 | 143.6 | P12:500-161:EES-EAI:M:NEW_MAD:PORTGV:WMPEHV:8BHAMSTE:HATI_S:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.0612 | 143.61 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.0612 | 143.62 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.0612 | 144.05 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.0612 | 145.31 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06121 | 145.91 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06121 | 146.77 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06121 | 148.44 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06122 | 144.08 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06128 | 142.63 | 506952 CENTRTN5 161 506980 SHIPERD5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06131 | 143.37 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06131 | 145.94 | P12:345:OKGE:BKRBKR400:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06134 | 146.57 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06142 | 150.38 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06142 | 151.14 | P42:345:OKGE:SB_OPKY7319:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06142 | 151.15 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06142 | 153.7 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06142 | 155.29 | Potential P4 Event - POI 560053_1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06142 | 155.31 | Potential P4 Event - POI 560053_2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06142 | 155.34 | Potential P4 Event - POI 560053_0 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06142 | 161.31 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06159 | 144.97 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06159 | 144.98 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.0617 | 142.91 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.0617 | 148.47 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06197 | 159.83 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06197 | 162.09 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06202 | 157.82 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06202 | 161.69 | Potential P4 Event - POI 773480_2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06202 | 161.72 | Potential P4 Event - POI 773480_0 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06202 | 161.77 | Potential P4 Event - POI 773480_1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06202 | 165.14 | Potential P4 Event - POI 532793_13 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06202 | 165.15 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06202 | 165.15 | Potential P4 Event - POI 532793_16 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06202 | 167.53 | Potential P4 Event - POI 532793_18 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06204 | 162.17 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06204 | 162.17 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06221 | 144.28 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06221 | 145.47 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06221 | 147.34 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06231 | 143.21 | 547579 COM381T2 69.0 547590 QUA377 2 69.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06231 | 143.75 | 547579 COM381T2 69.0 547583 FRL363 2 69.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06239 | 154.76 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06244 | 144.15 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06327 | 149.71 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06361 | 148.2 | 512632 AFTON 5 161 3WXFMR AFTAUTO1 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06403 | 154.76 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06434 | 151.3 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06435 | 157.69 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06475 | 163.38 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06495 | 148.24 | 512654 PENSA 5 161 3WXFMR PENAUTO1 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 194 | 194 | 0.06932 | 163.87 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06217 | 112.88 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06217 | 113.04 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0634 | 125.42 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06347 | 108.21 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06348 | 107.37 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06352 | 109.85 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06352 | 110.79 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06353 | 107.9 | 547498 STL439 5 161 547657 S3G439 1 18.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06368 | 107.51 | 512631 MIAMI 5 161 3WXFMR MIAAUTO2 2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06374 | 107.64 | P23:345:AEPW:NES CB 3417B NBTB:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06374 | 107.64 | P41:345:AEPW:NES CB 3417B NBTB+FAULT:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06384 | 106.27 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06384 | 106.29 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06389 | 105.76 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06394 | 106.16 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06394 | 106.17 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06395 | 110.49 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06396 | 104.99 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06396 | 105.85 | P12:EHV:EES::7STFRAN!:7GOBKNOB%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06396 | 107.58 | P23:345:WERE:WICH-345-116:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06397 | 104.78 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06397 | 104.81 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06397 | 105.12 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06397 | 107.79 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06397 | 111.09 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06397 | 111.09 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06398 | 105 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06398 | 105.17 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06398 | 105.17 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06398 | 105.3 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06398 | 108.16 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06398 | 108.78 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 104.8 | 659336 TANDE___-BE3 345 659479 TRADEWND-UA3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 104.86 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 104.86 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 105.22 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 105.25 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 105.27 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 105.39 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 105.47 | 772981 GEN-2023-050 345 772982 G23-050XFMR1 34.5 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 105.47 | 772981 GEN-2023-050 345 772985 G23-050XFMR2 34.5 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 105.55 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 105.66 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 105.75 | GEN-2023-075_POI_773480_Generator_outage | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 105.84 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 105.84 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 105.87 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 105.93 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 105.99 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 106.17 | P23:345:XEL:8N8 MNN | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 106.18 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 106.18 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 106.19 | P23:345:XEL:8N22 SHC | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 106.2 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 106.2 | P23:345:XEL:8N17 SHC | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 106.24 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 106.29 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 106.38 | GEN-2023-050_POI_532793_Generator_outage | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 106.46 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 106.63 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 106.67 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 106.67 | P23:345:MEC:CBEC 908 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 106.75 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 106.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 106.88 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 106.89 | P23:345:MEC:CBEC 905 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 107.15 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 107.21 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 107.33 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 107.42 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 107.49 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 108.88 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 109 | 764300 GEN-2020-079 161 764310 G20-079-TAP 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 109 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06399 | 109 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.064 | 104.92 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.064 | 105.32 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.064 | 105.62 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.064 | 105.99 | P23:345:MEC:LOUISA 954 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.064 | 106.38 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.064 | 106.38 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.064 | 106.53 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.064 | 106.86 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.064 | 107.07 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.064 | 107.94 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06401 | 105.31 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06401 | 105.44 | P23:345:AMMO::MONTGOMERY:V43:: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06401 | 105.59 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06401 | 106.6 | 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06401 | 106.8 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06401 | 106.81 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06401 | 106.81 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06401 | 107.93 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06401 | 108.47 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06402 | 105.16 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06402 | 106.36 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06402 | 108.5 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06403 | 105.71 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06403 | 105.75 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06403 | 105.8 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06403 | 106.84 | P12:500-161:EES-EAI:M:NEW_MAD:PORTGV:WMPEHV:8BHAMSTE:HATI_S:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06403 | 106.86 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06403 | 106.93 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06403 | 107.32 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06403 | 108.95 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06404 | 109.75 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06404 | 111.94 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06405 | 107.33 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06408 | 105.68 | 506952 CENTRTN5 161 506980 SHIPERD5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06411 | 106.27 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06415 | 109.38 | P12:345:OKGE:BKRBKR400:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06428 | 114.06 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06428 | 115.05 | P42:345:OKGE:SB_OPKY7319:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06428 | 115.05 | P42:345:OKGE:SB_OPKY7388:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06428 | 115.06 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06428 | 117.39 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06428 | 119.46 | Potential P4 Event - POI 560053_1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06428 | 119.49 | Potential P4 Event - POI 560053_2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06428 | 119.5 | Potential P4 Event - POI 560053_0 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06428 | 124.91 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06434 | 107.31 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06434 | 107.32 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06454 | 106.25 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06463 | 112.5 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06489 | 107.06 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06489 | 108.31 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06489 | 109.32 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06492 | 124.63 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06492 | 126.92 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06499 | 122.41 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06499 | 126.67 | Potential P4 Event - POI 773480_0 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06499 | 126.67 | Potential P4 Event - POI 773480_2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06499 | 126.73 | Potential P4 Event - POI 773480_1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06499 | 129.88 | Potential P4 Event - POI 532793_13 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06499 | 129.91 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06499 | 129.91 | Potential P4 Event - POI 532793_16 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06499 | 132.47 | Potential P4 Event - POI 532793_18 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06501 | 126.99 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06501 | 126.99 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06587 | 123.77 | 510417 VINTAJC4 138 547486 HOC404 4 138 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06587 | 123.77 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06592 | 111.63 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06624 | 118.19 | 300852 2MIAETP 69.0 512630 MIAMI 2 69.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06668 | 109.08 | 547579 COM381T2 69.0 547590 QUA377 2 69.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06668 | 110.2 | 547579 COM381T2 69.0 547583 FRL363 2 69.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06701 | 110.84 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06701 | 118.68 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06709 | 117.58 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06724 | 114.22 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.07289 | 127.1 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06385 | 160.71 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06385 | 160.87 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06441 | 165.14 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06441 | 166.18 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06467 | 178.83 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0649 | 156.89 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06492 | 155.85 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06495 | 156.59 | 547498 STL439 5 161 547657 S3G439 1 18.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06514 | 156 | P23:345:AEPW:NES CB 3417B NBTB:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06514 | 156 | P41:345:AEPW:NES CB 3417B NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06515 | 155.65 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06515 | 155.75 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06517 | 163.6 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06526 | 154.45 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0653 | 155.01 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0653 | 155.02 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06531 | 158.67 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06532 | 154.75 | P12:EHV:EES::7STFRAN!:7GOBKNOB%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06532 | 156.25 | P23:345:WERE:WICH-345-116:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06533 | 153.48 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06533 | 153.51 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06533 | 153.67 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06533 | 153.75 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06533 | 156.57 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06533 | 156.63 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06533 | 159.29 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06533 | 159.29 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06534 | 153.73 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06534 | 153.84 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06534 | 153.84 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06534 | 154.04 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06534 | 154.06 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06534 | 154.7 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06534 | 157.66 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 153.5 | 659336 TANDE___-BE3 345 659479 TRADEWND-UA3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 153.55 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 153.55 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 153.61 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 153.96 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 154.03 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 154.04 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 154.06 | 772981 GEN-2023-050 345 772982 G23-050XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 154.08 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 154.14 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 154.35 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 154.38 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 154.53 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 154.53 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 154.65 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 154.78 | P23:345:MEC:LOUISA 954 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 154.81 | 771661 GEN-2022-234 138 771662 G22-234XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 154.81 | GEN-2022-234_POI_771660_Generator_outage | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 154.85 | GEN-2023-050_POI_532793_Generator_outage | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 154.89 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 154.9 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 154.91 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 154.91 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 154.92 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 154.92 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 155.01 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 155.02 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 155.13 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 155.15 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 155.3 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 155.34 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 155.34 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 155.34 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 155.39 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 155.5 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 155.52 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 155.53 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 155.8 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 155.84 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 156.03 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 156.1 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 156.44 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 156.59 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 156.97 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 157.34 | 764300 GEN-2020-079 161 764310 G20-079-TAP 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 157.34 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 157.34 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06536 | 153.75 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06536 | 153.9 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06536 | 154.44 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06536 | 155.22 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06536 | 155.22 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06536 | 155.62 | 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06536 | 155.7 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06536 | 155.83 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06536 | 155.85 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06536 | 155.87 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06536 | 156.89 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06536 | 156.94 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06536 | 157.31 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06537 | 154.46 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06538 | 154.37 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06538 | 154.4 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06538 | 154.46 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06538 | 155.54 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06538 | 155.77 | P12:500-161:EES-EAI:M:NEW_MAD:PORTGV:WMPEHV:8BHAMSTE:HATI_S:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06538 | 155.78 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06538 | 155.78 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06538 | 156.22 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06538 | 157.5 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06539 | 158.12 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06539 | 159.01 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06539 | 160.53 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0654 | 156.25 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0654 | 173.66 | Potential P4 Event - POI 532794_2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06546 | 154.84 | 506952 CENTRTN5 161 506980 SHIPERD5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06549 | 155.59 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06549 | 158.06 | P12:345:OKGE:BKRBKR400:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06553 | 159.12 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06555 | 154.14 | 547561 NOL443 2 69.0 547566 AND322 2 69.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06555 | 154.52 | 547561 NOL443 2 69.0 547610 NOL435 2 69.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06557 | 173.72 | Potential P4 Event - POI 532794_5 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0656 | 162.45 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0656 | 163.22 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0656 | 163.22 | P42:345:OKGE:SB_OPKY7319:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0656 | 165.77 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0656 | 167.37 | Potential P4 Event - POI 560053_1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0656 | 167.37 | Potential P4 Event - POI 560053_2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0656 | 167.42 | Potential P4 Event - POI 560053_0 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0656 | 173.41 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0658 | 157.36 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0658 | 157.38 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06584 | 160.24 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 155.14 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06611 | 161.76 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06614 | 171.88 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06614 | 174.16 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06619 | 169.72 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06619 | 173.66 | Potential P4 Event - POI 773480_1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06619 | 177.02 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06619 | 177.02 | Potential P4 Event - POI 532793_13 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06619 | 177.02 | Potential P4 Event - POI 532793_16 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06619 | 179.41 | Potential P4 Event - POI 532793_18 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06621 | 174.23 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06621 | 174.23 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06642 | 156.51 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06642 | 157.74 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06642 | 159.7 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06652 | 156.04 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line