Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06746 | 161.89 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06829 | 167.29 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06871 | 170.76 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06873 | 164.12 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06915 | 176.91 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.07256 | 167.27 | 512654 PENSA 5 161 3WXFMR PENAUTO1 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.07381 | 176.85 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06385 | 165.57 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06385 | 165.72 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06441 | 169.99 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06441 | 171.04 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06467 | 183.73 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0649 | 161.74 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06492 | 160.7 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06495 | 161.45 | 547498 STL439 5 161 547657 S3G439 1 18.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06514 | 160.84 | P23:345:AEPW:NES CB 3417B NBTB:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06514 | 160.84 | P41:345:AEPW:NES CB 3417B NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06515 | 160.5 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06515 | 160.6 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06517 | 168.49 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06526 | 159.29 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0653 | 159.86 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0653 | 159.86 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06531 | 163.53 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06532 | 159.6 | P12:EHV:EES::7STFRAN!:7GOBKNOB%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06532 | 161.1 | P23:345:WERE:WICH-345-116:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06533 | 158.32 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06533 | 158.35 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06533 | 158.51 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06533 | 158.59 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06533 | 161.42 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06533 | 161.49 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06533 | 164.16 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06533 | 164.16 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06534 | 158.57 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06534 | 158.68 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06534 | 158.68 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06534 | 158.88 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06534 | 158.9 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06534 | 159.55 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06534 | 162.52 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 158.34 | 659336 TANDE___-BE3 345 659479 TRADEWND-UA3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 158.39 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 158.39 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 158.44 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 158.8 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 158.87 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 158.88 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 158.89 | 772981 GEN-2023-050 345 772985 G23-050XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 158.93 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 158.98 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 159.19 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 159.23 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 159.37 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 159.37 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 159.49 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 159.62 | P23:345:MEC:LOUISA 954 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 159.65 | 771661 GEN-2022-234 138 771662 G22-234XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 159.65 | GEN-2022-234_POI_771660_Generator_outage | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 159.69 | GEN-2023-050_POI_532793_Generator_outage | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 159.74 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 159.75 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 159.76 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 159.76 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 159.76 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 159.77 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 159.85 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 159.87 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 159.98 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 160 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 160.15 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 160.18 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 160.18 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 160.19 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 160.24 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 160.35 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 160.37 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 160.38 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 160.65 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 160.69 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 160.88 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 160.96 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 161.3 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 161.46 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 161.82 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 162.2 | 764300 GEN-2020-079 161 764310 G20-079-TAP 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 162.2 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06535 | 162.2 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06536 | 158.58 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06536 | 158.74 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06536 | 159.28 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06536 | 160.07 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06536 | 160.07 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06536 | 160.48 | 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06536 | 160.55 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06536 | 160.69 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06536 | 160.7 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06536 | 160.71 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06536 | 161.74 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06536 | 161.8 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06536 | 162.17 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06537 | 159.31 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06538 | 159.21 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06538 | 159.25 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06538 | 159.3 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06538 | 160.39 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06538 | 160.62 | P12:500-161:EES-EAI:M:NEW_MAD:PORTGV:WMPEHV:8BHAMSTE:HATI_S:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06538 | 160.63 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06538 | 160.63 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06538 | 161.07 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06538 | 162.37 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06539 | 162.98 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06539 | 163.88 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06539 | 165.4 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0654 | 161.1 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0654 | 178.6 | Potential P4 Event - POI 532794_2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06546 | 159.68 | 506952 CENTRTN5 161 506980 SHIPERD5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06549 | 160.43 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06549 | 162.91 | P12:345:OKGE:BKRBKR400:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06553 | 164.01 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06555 | 158.98 | 547561 NOL443 2 69.0 547566 AND322 2 69.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06555 | 159.36 | 547561 NOL443 2 69.0 547610 NOL435 2 69.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06557 | 178.66 | Potential P4 Event - POI 532794_5 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0656 | 167.32 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0656 | 168.09 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0656 | 168.09 | P42:345:OKGE:SB_OPKY7319:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0656 | 170.66 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0656 | 172.26 | Potential P4 Event - POI 560053_1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0656 | 172.27 | Potential P4 Event - POI 560053_2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0656 | 172.31 | Potential P4 Event - POI 560053_0 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0656 | 178.35 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0658 | 162.22 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.0658 | 162.23 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06584 | 165.1 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06591 | 159.99 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06611 | 166.61 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06614 | 176.76 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06614 | 179.05 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06619 | 174.6 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06619 | 178.57 | Potential P4 Event - POI 773480_1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06619 | 181.94 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06619 | 181.94 | Potential P4 Event - POI 532793_16 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06619 | 181.95 | Potential P4 Event - POI 532793_13 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06619 | 184.34 | Potential P4 Event - POI 532793_18 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06621 | 179.13 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06621 | 179.13 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06642 | 161.36 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06642 | 162.59 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06642 | 164.56 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06652 | 160.88 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06746 | 166.75 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06829 | 172.19 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06871 | 175.66 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06873 | 169 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.06915 | 181.84 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.07256 | 172.12 | 512654 PENSA 5 161 3WXFMR PENAUTO1 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 194 | 194 | 0.07381 | 181.75 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-055 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.06534 | 101.13 | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-057 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.05459 | 101.13 | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-057 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.06483 | 100.54 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-057 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.06483 | 100.54 | Potential P4 Event - POI 532794_9 | Cumulative Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-057 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.06493 | 100.68 | Potential P4 Event - POI 532794_5 | Cumulative Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-063 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.0634 | 101.13 | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-063 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.07682 | 100.68 | Potential P4 Event - POI 532794_5 | Cumulative Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-063 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.07689 | 100.54 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-063 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.07689 | 100.54 | Potential P4 Event - POI 532794_9 | Cumulative Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-064 | FROM->TO | 507189 NHUNTNT5 161 775580 G23-180-TAP 161 1 | 158 | 178 | 0.10333 | 101.74 | 515261 BONANZT5 161 515299 BEVYTAP5 161 1 | Cumulative Impact | Rebuild the existing NHUNTNT5 to G23-180-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-069 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.08073 | 109.58 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-069 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.08073 | 109.58 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-069 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.08073 | 109.58 | Potential P4 Event - POI 508359_5 | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-069 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.1224 | 105.14 | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-069 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.1224 | 105.14 | 521157 HUGO 7 345 3WXFMR HUGO 1 1 | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-075 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.09567 | 101.13 | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-075 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.60288 | 100.68 | Potential P4 Event - POI 532794_5 | Cumulative Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-075 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.60306 | 100.54 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-075 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.60306 | 100.54 | Potential P4 Event - POI 532794_9 | Cumulative Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-076 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.09567 | 101.13 | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-076 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.60288 | 100.68 | Potential P4 Event - POI 532794_5 | Cumulative Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-076 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.60306 | 100.54 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-076 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.60306 | 100.54 | Potential P4 Event - POI 532794_9 | Cumulative Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-088 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.15114 | 100.03 | P12:138:AEPW:HENRYET4:WELETK4::: | Cumulative Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-088 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.05143 | 100.54 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-088 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.05143 | 100.54 | Potential P4 Event - POI 532794_9 | Cumulative Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-088 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.05146 | 100.68 | Potential P4 Event - POI 532794_5 | Cumulative Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-092 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.15624 | 109.58 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-092 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.15624 | 109.58 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-092 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.15624 | 109.58 | Potential P4 Event - POI 508359_5 | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-092 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.42371 | 105.14 | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-092 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.42371 | 105.14 | 521157 HUGO 7 345 3WXFMR HUGO 1 1 | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 435 | 435 | 1 | 108.78 | 523777 WHEELER 6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-101 | FROM->TO | 523777 WHEELER 6 230 774000 G23-101-TAP 230 1 | 353 | 353 | 1 | 135.11 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing WHEELER 6 to G23-101-TAP 230 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.68783 | 142.32 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.68783 | 142.32 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.68783 | 142.32 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.69387 | 100.32 | GEN-2023-102_POI_515852_Generator_outage | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.70679 | 111 | Potential P4 Event - POI 515852_4 | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.70679 | 111 | Potential P4 Event - POI 515852_8 | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.70688 | 104.64 | Potential P4 Event - POI 515375_27 | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.70688 | 104.64 | Potential P4 Event - POI 515375_36 | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.70952 | 109.17 | P42:345:OKGE:SB_REOW7312:::: | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.70952 | 109.17 | Potential P4 Event - POI 515543_0 | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.70964 | 108.43 | P12:345:OKGE:BKRBKR421:::: | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.70964 | 109.31 | Potential P4 Event - POI 515543_1 | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.70976 | 107.63 | P12:345:OKGE:BKRBKR400:::: | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.71006 | 108.25 | Potential P4 Event - POI 514715_2 | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.71102 | 101.58 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.71102 | 104.82 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.71107 | 100.32 | 515852 DGRASSE7 345 776821 GEN-2023-102 345 1 | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.71117 | 100.5 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.7113 | 100.88 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.71137 | 101.67 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.71139 | 101.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.71141 | 100.57 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.71158 | 102.96 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.71474 | 100.49 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.71474 | 100.81 | P12:138:WFEC:MOORELND_CLEOCRNR:::: | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.71474 | 100.85 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-104 | FROM->TO | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 160 | 187 | 0.71604 | 100.53 | 521065 TALOGA 4 138 765215 G20-010-TAP 138 1 | Cumulative Impact | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-132 | FROM->TO | 338758 5HEBER.N# 161 505422 GREERSF5 161 1 | 205 | 205 | 1 | 111.47 | 505418 JONESBO5 161 774620 G23-132-TAP 161 1 | Cumulative Impact | Rebuild the existing 5HEBER.N# to GREERSF5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-134 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.13392 | 100.03 | P12:138:AEPW:HENRYET4:WELETK4::: | Cumulative Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-134 | FROM->TO | 515077 FIXICO 2 69.0 997806 FIXICO4 69.0 4 | 62 | 67 | 0.20772 | 107.03 | 510902 WELETK4 138 774660 G23-134-TAP 138 1 | Cumulative Impact | Upgrade the existing FIXICO4 138/69 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-134 | FROM->TO | 515078 FIXICO 4 138 997806 FIXICO4 69.0 4 | 62 | 67 | 0.20772 | 106.29 | 510902 WELETK4 138 774660 G23-134-TAP 138 1 | Cumulative Impact | Upgrade the existing FIXICO4 138/69 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-135 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.28908 | 109.58 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-135 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.28908 | 109.58 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-135 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.28908 | 109.58 | Potential P4 Event - POI 508359_5 | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-138 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.06599 | 101.13 | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-151 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.10104 | 109.58 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-151 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.10104 | 109.58 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-151 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.10104 | 109.58 | Potential P4 Event - POI 508359_5 | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-180 | FROM->TO | 507189 NHUNTNT5 161 775580 G23-180-TAP 161 1 | 158 | 178 | 0.59014 | 101.74 | 515261 BONANZT5 161 515299 BEVYTAP5 161 1 | Cumulative Impact | Rebuild the existing NHUNTNT5 to G23-180-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-205 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.16354 | 100.03 | P12:138:AEPW:HENRYET4:WELETK4::: | Cumulative Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-205 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.05131 | 100.54 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-205 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.05131 | 100.54 | Potential P4 Event - POI 532794_9 | Cumulative Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-205 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.05134 | 100.68 | Potential P4 Event - POI 532794_5 | Cumulative Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-210 | FROM->TO | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 151 | 152 | 0.0608 | 100.03 | P12:138:AEPW:HENRYET4:WELETK4::: | Cumulative Impact | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 514803 SOONER 7 345 515576 RANCHRD7 345 1 | 1716 | 1793 | 1 | 101.3 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 514803 SOONER 7 345 515576 RANCHRD7 345 1 | 1716 | 1793 | 1 | 101.31 | Potential P4 Event - POI 532794_2 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 514803 SOONER 7 345 515576 RANCHRD7 345 1 | 1716 | 1793 | 1 | 101.32 | Potential P4 Event - POI 532794_5 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 514803 SOONER 7 345 515576 RANCHRD7 345 1 | 1716 | 1793 | 1 | 101.33 | Potential P4 Event - POI 532794_7 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.17603 | 101.13 | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.058 | 100.54 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.058 | 100.54 | Potential P4 Event - POI 532794_9 | Cumulative Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-211 | FROM->TO | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 1294 | 1294 | 0.05817 | 100.68 | Potential P4 Event - POI 532794_5 | Cumulative Impact | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-212 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.25637 | 109.58 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-212 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.25637 | 109.58 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-212 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.25637 | 109.58 | Potential P4 Event - POI 508359_5 | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-213 | FROM->TO | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 878 | 956 | 0.06082 | 101.13 | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-227 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.12599 | 109.58 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-227 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.12599 | 109.58 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27SP | GEN-2023-227 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.12599 | 109.58 | Potential P4 Event - POI 508359_5 | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-009 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.17539 | 100.46 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-009 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.17539 | 100.46 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-009 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.17539 | 100.46 | Potential P4 Event - POI 508359_5 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-009 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.16671 | 112.2 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-009 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.16671 | 112.2 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-009 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.16671 | 112.2 | Potential P4 Event - POI 508359_5 | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-009 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.30499 | 102.7 | P23:345:AEPW:VALLIANT CB 3413A NBTB:::: | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-009 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.30499 | 102.7 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT:::: | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-009 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.30735 | 105.06 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-009 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.49363 | 110.16 | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-009 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.49363 | 110.16 | 521157 HUGO 7 345 3WXFMR HUGO 1 1 | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-022 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.06246 | 100.46 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-022 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.06246 | 100.46 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-022 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.06246 | 100.46 | Potential P4 Event - POI 508359_5 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.18061 | 120.84 | P12:161:AEPW-EMDE:FLINTCR5:739952::: | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.1848 | 106.93 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.1848 | 107.04 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20285 | 100.83 | Potential P4 Event - POI 509745_2 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20285 | 101.05 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20299 | 100.63 | Potential P4 Event - POI 509745_0 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20299 | 100.73 | Potential P4 Event - POI 509745_1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20583 | 108.85 | 512650 GRDA1 7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20583 | 114.3 | Potential P4 Event - POI 774740_0 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20583 | 114.3 | Potential P4 Event - POI 774740_2 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20583 | 114.46 | Potential P4 Event - POI 774740_1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20583 | 117.52 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20592 | 108.01 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20592 | 108.01 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510402 GROVE 4 138 997939 GROVE 138 1 | 112 | 112 | 0.20592 | 108.43 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.18061 | 121.81 | P12:161:AEPW-EMDE:FLINTCR5:739952::: | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.1848 | 107.43 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.1848 | 107.57 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20285 | 101.89 | Potential P4 Event - POI 509745_2 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20285 | 102.11 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20299 | 101.7 | Potential P4 Event - POI 509745_0 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20299 | 101.79 | Potential P4 Event - POI 509745_1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20583 | 110.11 | 512650 GRDA1 7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20583 | 115.72 | Potential P4 Event - POI 774740_0 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20583 | 115.72 | Potential P4 Event - POI 774740_2 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20583 | 115.91 | Potential P4 Event - POI 774740_1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20583 | 119 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20592 | 109.02 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20592 | 109.02 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-027 | FROM->TO | 510411 GROVE 5 161 997939 GROVE 138 1 | 112 | 112 | 0.20592 | 109.51 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Upgrade the existing GROVE 161/138 kV Transformer
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | 335 | 335 | 1 | 111.67 | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | Cumulative Impact | DRYGULCH5 to G23-028-TAP 161 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.1324 | 130.49 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.1324 | 130.53 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13336 | 129.02 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13336 | 129.15 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13388 | 125.59 | P12:345:WERE:NRSS-N345-345:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13394 | 125.28 | P12:345:WERE:CANR-G17-345:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13394 | 125.31 | P23:345:WERE:CANR-BKRS:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13474 | 124.65 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13476 | 124.32 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13476 | 124.41 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.1348 | 124.39 | P23:345:AEPW:NES CB 3417B NBTB:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.1348 | 124.39 | P41:345:AEPW:NES CB 3417B NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13489 | 123.6 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13492 | 126.5 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13492 | 126.5 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13495 | 123.99 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13495 | 124 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13496 | 126.49 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13497 | 122.91 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13497 | 134.01 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13498 | 122.94 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13498 | 124.49 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13499 | 122.91 | 659348 LC_CT1-3-BE7 115 659349 LC_SWY.N-BE7 115 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13499 | 123.17 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13499 | 123.17 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13499 | 123.17 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13499 | 124.41 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13499 | 125.59 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13499 | 127.89 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13499 | 127.89 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 122.66 | 655846 F9______-MK7 115 655872 G9TAP___-MK7 115 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 122.93 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 122.96 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 122.96 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 123.03 | P21:161:ALTW:AUTO-SINGLE:LIMECKL15:CLKREACT5:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 123.08 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 123.1 | 672650 NIPAWIN 4 230 672351 NIPAWIN 2G 13.8 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 123.14 | 773481 GEN-2023-075 345 773482 G23-075XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 123.14 | 773488 G23-075XFMRH 345 773485 G23-075XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 123.2 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 123.23 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 123.24 | GEN-2023-231_POI_776600_Generator_outage | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 123.24 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 123.41 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 123.52 | GEN-2023-075_POI_773480_Generator_outage | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 123.53 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 123.53 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 123.61 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 123.64 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 123.64 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 123.64 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 123.64 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 123.73 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 123.76 | P11:20:AMMO:1LAB G1:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 123.9 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 123.92 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 123.92 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 123.95 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 123.95 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 123.95 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 123.95 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 123.98 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 124.03 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 124.06 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 124.06 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 124.13 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 124.22 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 124.22 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 124.28 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 124.29 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 124.31 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 124.38 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 124.38 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 124.59 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 124.63 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 125.09 | 547501 RIV453 5 161 547643 R13G167 13.8 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 125.3 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.135 | 125.4 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13501 | 123.05 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13501 | 123.81 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13501 | 123.96 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13501 | 123.96 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13501 | 123.96 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13501 | 123.96 | P23:500:EES:PERYVL:R7372 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13501 | 125.01 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13502 | 123.14 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13502 | 123.4 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13502 | 123.42 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13502 | 123.46 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13503 | 123.55 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13503 | 123.63 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13504 | 123.96 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13504 | 124.34 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13505 | 124.02 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13505 | 124.08 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13505 | 124.12 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13505 | 124.9 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13505 | 125.65 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13506 | 124.11 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13507 | 124.48 | P23:500:EAI:NBF_PLEASANT | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13507 | 125.06 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13507 | 127.45 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13507 | 127.88 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13508 | 127.2 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.1351 | 123.84 | 506952 CENTRTN5 161 506980 SHIPERD5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13512 | 124.49 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13514 | 125.74 | P12:345:OKGE:BKRBKR400:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13519 | 127.86 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13521 | 124.02 | P23:500:EES-EAI:MABELV:B5918:_1:: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13525 | 128.69 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13525 | 129.2 | P42:345:OKGE:SB_OPKY7388:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13525 | 129.21 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13525 | 129.21 | P42:345:OKGE:SB_OPKY7319:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13525 | 131.26 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13525 | 132.36 | Potential P4 Event - POI 560053_1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13525 | 132.38 | Potential P4 Event - POI 560053_2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13525 | 132.39 | Potential P4 Event - POI 560053_0 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13525 | 136.66 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.1354 | 128.17 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13551 | 124.17 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13551 | 124.17 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13555 | 138.13 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13563 | 138.13 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13563 | 138.13 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13567 | 126.52 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13567 | 127.92 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13567 | 130 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13567 | 134.61 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13567 | 137.83 | Potential P4 Event - POI 773480_2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13567 | 137.84 | Potential P4 Event - POI 773480_1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13567 | 137.86 | Potential P4 Event - POI 773480_0 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13567 | 140.73 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13567 | 140.73 | Potential P4 Event - POI 532793_16 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13567 | 140.74 | Potential P4 Event - POI 532793_13 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13567 | 141.23 | Potential P4 Event - POI 532793_18 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13575 | 124.52 | P12:500:OKGE-EESAR:OKGE-EESEAI:BKRBKR317::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13575 | 124.52 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13588 | 125.57 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13602 | 130.65 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13709 | 124.78 | 547579 COM381T2 69.0 547590 QUA377 2 69.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13709 | 125.22 | 547579 COM381T2 69.0 547583 FRL363 2 69.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13751 | 135.09 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13805 | 131.36 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.13806 | 136.38 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.1389 | 140.99 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.14257 | 139.69 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.14295 | 129.16 | 512632 AFTON 5 161 3WXFMR AFTAUTO1 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.14425 | 139.35 | 512633 AFTON 2 69.0 512708 FAIRTAP2 69.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.14658 | 128.94 | 512654 PENSA 5 161 3WXFMR PENAUTO1 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.30765 | 141.88 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13274 | 116.92 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13274 | 116.95 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13455 | 110.57 | P12:345:WERE:NRSS-N345-345:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13459 | 112.44 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13462 | 110.25 | P23:345:WERE:CANR-BKRS:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13501 | 109.96 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13559 | 109.19 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13565 | 109.13 | P23:345:AEPW:NES CB 3417B NBTB:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13565 | 109.13 | P41:345:AEPW:NES CB 3417B NBTB+FAULT:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13569 | 108.37 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13569 | 108.45 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13576 | 108.08 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13583 | 110.09 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13583 | 110.09 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13583 | 112.31 | P12:161:AEPW-EMDE:FLINTCR5:739952::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13585 | 108.41 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13585 | 108.43 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13585 | 125.42 | 510417 VINTAJC4 138 547486 HOC404 4 138 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13585 | 125.42 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13586 | 112.03 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13587 | 107.19 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13587 | 109.24 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13588 | 107.18 | 659348 LC_CT1-3-BE7 115 659349 LC_SWY.N-BE7 115 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13588 | 107.23 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13588 | 107.44 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13588 | 107.51 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13588 | 107.52 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13588 | 110.55 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13588 | 113.46 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13588 | 113.46 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13589 | 107.12 | 655841 ARNEGARD-MK7 115 659346 LC_SWY.S-BE7 115 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13589 | 107.35 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13589 | 107.51 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 107.2 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 107.26 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 107.26 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 107.33 | P21:161:ALTW:AUTO-SINGLE:LIMECKL15:CLKREACT5:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 107.43 | 672650 NIPAWIN 4 230 672350 NIPAWIN 1G 13.8 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 107.54 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 107.56 | 773481 GEN-2023-075 345 773482 G23-075XFMR1 34.5 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 107.56 | 773488 G23-075XFMRH 345 773485 G23-075XFMR2 34.5 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 107.6 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 107.63 | GEN-2023-231_POI_776600_Generator_outage | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 107.68 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 107.97 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 107.98 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 107.98 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 108.06 | P11:20:AMMO:1LAB G1:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 108.11 | GEN-2023-075_POI_773480_Generator_outage | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 108.13 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 108.13 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 108.14 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 108.14 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 108.2 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 108.27 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 108.42 | P23:345:XEL:8N8 MNN | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 108.47 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 108.47 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 108.47 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 108.47 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 108.47 | P23:345:XEL:8N22 SHC | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 108.48 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 108.48 | P23:345:XEL:8N17 SHC | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 108.57 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 108.67 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 108.67 | P23:345:MEC:CBEC 908 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 108.71 | 773480 G23-075-TAP 345 773481 GEN-2023-075 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 108.76 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 108.78 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 108.87 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 108.88 | P23:345:MEC:CBEC 905 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 108.89 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 109 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 109.07 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 109.35 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 109.41 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 109.66 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 109.77 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 109.98 | 547501 RIV453 5 161 547643 R13G167 13.8 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1359 | 110.6 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13591 | 108.1 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13591 | 108.21 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13591 | 108.38 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13591 | 108.38 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13591 | 108.38 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13591 | 108.38 | P23:500:EES:PERYVL:R7372 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13591 | 109.32 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13592 | 107.39 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13592 | 107.41 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13593 | 107.76 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13593 | 107.78 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13593 | 107.83 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13593 | 107.91 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13593 | 108.01 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13594 | 108.36 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13594 | 108.8 | P12:500-161:EES-EAI:M:NEW_MAD:PORTGV:WMPEHV:8BHAMSTE:HATI_S:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13594 | 108.82 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13595 | 108.31 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13595 | 108.37 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13595 | 108.52 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13595 | 108.95 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13595 | 109.42 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13595 | 110.3 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13596 | 108.49 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13597 | 109.57 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13597 | 112.06 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13598 | 112.52 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13599 | 112.28 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.136 | 108.63 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13606 | 110.53 | P12:345:OKGE:BKRBKR400:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13612 | 108.43 | P23:500:EES-EAI:MABELV:B5918:_1:: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13619 | 114.12 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13619 | 114.94 | P42:345:OKGE:SB_OPKY7388:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13619 | 114.96 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13619 | 114.96 | P42:345:OKGE:SB_OPKY7319:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13619 | 117.16 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13619 | 118.95 | Potential P4 Event - POI 560053_1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13619 | 118.97 | Potential P4 Event - POI 560053_2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13619 | 118.99 | Potential P4 Event - POI 560053_0 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13619 | 123.58 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13639 | 113.82 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13642 | 108.54 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13642 | 108.54 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13649 | 110.5 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13649 | 112.16 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13649 | 113.51 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13654 | 125.95 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13664 | 125.89 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13664 | 125.89 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13668 | 108.94 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13668 | 121.64 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13668 | 125.79 | Potential P4 Event - POI 773480_1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13668 | 125.82 | Potential P4 Event - POI 773480_0 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13668 | 125.83 | Potential P4 Event - POI 773480_2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13668 | 128.99 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13668 | 128.99 | Potential P4 Event - POI 532793_13 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13668 | 128.99 | Potential P4 Event - POI 532793_16 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13668 | 129.62 | Potential P4 Event - POI 532793_18 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13683 | 114.47 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13802 | 113.84 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13862 | 120.84 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13881 | 120.59 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13903 | 116.38 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13933 | 109.89 | 512632 AFTON 5 161 3WXFMR AFTAUTO1 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.13952 | 124.82 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.14081 | 111.91 | 547579 COM381T2 69.0 547590 QUA377 2 69.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.14081 | 113.04 | 547579 COM381T2 69.0 547583 FRL363 2 69.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.14187 | 121.9 | 300852 2MIAETP 69.0 512630 MIAMI 2 69.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.14415 | 126.44 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.30516 | 127.14 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14599 | 143.86 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14599 | 143.98 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14602 | 141.47 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14602 | 141.52 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14752 | 136.56 | P12:345:WERE:NRSS-N345-345:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14757 | 136.25 | P12:345:WERE:CANR-G17-345:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14758 | 136.28 | P23:345:WERE:CANR-BKRS:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14789 | 136.11 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14836 | 135.67 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14838 | 135.35 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14838 | 135.45 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14843 | 135.39 | P23:345:AEPW:NES CB 3417B NBTB:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14843 | 135.39 | P41:345:AEPW:NES CB 3417B NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14851 | 134.58 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14854 | 137.78 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14854 | 137.78 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14858 | 134.97 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14858 | 134.99 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14859 | 137.44 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.1486 | 133.89 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.1486 | 135.48 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14861 | 133.89 | 659348 LC_CT1-3-BE7 115 659349 LC_SWY.N-BE7 115 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14861 | 133.93 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14861 | 134.15 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14861 | 134.15 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14861 | 134.16 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14861 | 136.59 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14861 | 138.9 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14861 | 138.9 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14861 | 140.66 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14862 | 134.07 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14862 | 134.22 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14862 | 134.52 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14862 | 135.45 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 133.64 | 655846 F9______-MK7 115 655872 G9TAP___-MK7 115 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 133.91 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 133.94 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 133.95 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 134.02 | P21:161:ALTW:AUTO-SINGLE:LIMECKL15:CLKREACT5:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 134.09 | 672650 NIPAWIN 4 230 672351 NIPAWIN 2G 13.8 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 134.12 | 773481 GEN-2023-075 345 773482 G23-075XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 134.12 | 773488 G23-075XFMRH 345 773485 G23-075XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 134.19 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 134.22 | GEN-2023-231_POI_776600_Generator_outage | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 134.23 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 134.39 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 134.5 | GEN-2023-075_POI_773480_Generator_outage | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 134.52 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 134.62 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 134.63 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 134.63 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 134.63 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 134.63 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 134.72 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 134.75 | P11:20:AMMO:1LAB G1:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 134.9 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 134.91 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 134.91 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 134.94 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 134.94 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 134.94 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 134.95 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 134.97 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 135.02 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 135.05 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 135.05 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 135.12 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 135.21 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 135.22 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 135.28 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 135.31 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 135.33 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 135.37 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 135.38 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 135.58 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 135.63 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 136.06 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 136.08 | 547501 RIV453 5 161 547643 R13G167 13.8 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 136.32 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14863 | 136.42 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14864 | 134.03 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14864 | 134.81 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14864 | 134.96 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14864 | 134.96 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14864 | 134.96 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14864 | 134.96 | P23:500:EES:PERYVL:R7372 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14865 | 134.12 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14865 | 134.37 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14865 | 134.39 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14865 | 134.43 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14866 | 134.53 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14866 | 134.62 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14866 | 134.94 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14867 | 135.1 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14867 | 135.35 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14868 | 135.01 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14868 | 135.06 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14868 | 135.92 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14868 | 136.67 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14869 | 135.09 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14869 | 136.08 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.1487 | 135.51 | P23:500:EAI:NBF_PLEASANT | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.1487 | 138.53 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.1487 | 138.97 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14871 | 134.56 | 547561 NOL443 2 69.0 547566 AND322 2 69.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14871 | 134.88 | 547561 NOL443 2 69.0 547610 NOL435 2 69.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14871 | 138.16 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14873 | 134.9 | 506952 CENTRTN5 161 506980 SHIPERD5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14875 | 135.55 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14877 | 136.71 | P12:345:OKGE:BKRBKR400:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14883 | 139.26 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14884 | 135.03 | P23:500:EES-EAI:MABELV:B5918:_1:: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14888 | 139.62 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14888 | 140.13 | P42:345:OKGE:SB_OPKY7388:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14888 | 140.14 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14888 | 140.14 | P42:345:OKGE:SB_OPKY7319:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14888 | 142.19 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14888 | 143.28 | Potential P4 Event - POI 560053_1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14888 | 143.3 | Potential P4 Event - POI 560053_2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14888 | 143.31 | Potential P4 Event - POI 560053_0 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14888 | 147.58 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.149 | 138.86 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14917 | 135.24 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14917 | 135.24 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14918 | 149.07 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14925 | 149.09 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14925 | 149.09 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14928 | 145.44 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14928 | 148.65 | Potential P4 Event - POI 773480_2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14928 | 148.66 | Potential P4 Event - POI 773480_1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14928 | 148.69 | Potential P4 Event - POI 773480_0 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14928 | 151.53 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14928 | 151.53 | Potential P4 Event - POI 532793_16 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14928 | 151.54 | Potential P4 Event - POI 532793_13 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14928 | 152.03 | Potential P4 Event - POI 532793_18 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14932 | 137.64 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14932 | 139.09 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14932 | 141.28 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14939 | 135.54 | P12:500:OKGE-EESAR:OKGE-EESEAI:BKRBKR317::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14939 | 135.54 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14944 | 136.33 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.14965 | 141.71 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.15121 | 146.44 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.15186 | 148.15 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.15188 | 142.94 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.15276 | 147.38 | 512650 GRDA1 7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.15276 | 153.15 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.15647 | 151.32 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.17074 | 146.05 | 512654 PENSA 5 161 3WXFMR PENAUTO1 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.34275 | 155.24 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512633 AFTON 2 69.0 512708 FAIRTAP2 69.0 1 | 72 | 72 | 0.05176 | 199 | P21:161:GRDA:MIAMI5-AFTON5:::HV: | Cumulative Impact | AFTON2 to FAIRTAP2 69 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14599 | 134.93 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14599 | 135.05 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14602 | 132.8 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14602 | 132.84 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14752 | 128.37 | P12:345:WERE:NRSS-N345-345:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14757 | 128.09 | P12:345:WERE:CANR-G17-345:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14758 | 128.12 | P23:345:WERE:CANR-BKRS:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14789 | 127.97 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14836 | 127.58 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14838 | 127.28 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14838 | 127.37 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14843 | 127.3 | P23:345:AEPW:NES CB 3417B NBTB:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14843 | 127.3 | P41:345:AEPW:NES CB 3417B NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14851 | 126.58 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14854 | 129.47 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14854 | 129.48 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14858 | 126.93 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14858 | 126.95 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14859 | 129.16 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.1486 | 125.96 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.1486 | 127.39 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14861 | 125.96 | 659348 LC_CT1-3-BE7 115 659349 LC_SWY.N-BE7 115 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14861 | 125.99 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14861 | 126.19 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14861 | 126.2 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14861 | 126.2 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14861 | 128.4 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14861 | 130.5 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14861 | 130.5 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14861 | 132.05 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14862 | 126.12 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14862 | 126.26 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14862 | 126.52 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14862 | 127.37 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 125.72 | 655845 GRDNCRK2-MK7 115 655879 OASIS___-MK7 115 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 125.98 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 126 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 126.01 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 126.07 | P21:161:ALTW:AUTO-SINGLE:LIMECKL15:CLKREACT5:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 126.13 | 672650 NIPAWIN 4 230 672350 NIPAWIN 1G 13.8 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 126.17 | 773481 GEN-2023-075 345 773482 G23-075XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 126.17 | 773488 G23-075XFMRH 345 773485 G23-075XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 126.23 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 126.25 | GEN-2023-231_POI_776600_Generator_outage | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 126.27 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 126.41 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 126.51 | GEN-2023-075_POI_773480_Generator_outage | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 126.53 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 126.61 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 126.62 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 126.62 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 126.63 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 126.63 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 126.7 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 126.74 | P11:20:AMMO:1LAB G1:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 126.86 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 126.88 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 126.88 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 126.9 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 126.9 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 126.91 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 126.91 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 126.93 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 126.98 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 127 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 127 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 127.07 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 127.15 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 127.15 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 127.22 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 127.24 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 127.27 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 127.29 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 127.3 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 127.48 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 127.52 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 127.91 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 127.94 | 547501 RIV453 5 161 547643 R13G167 13.8 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 128.16 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14863 | 128.25 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14864 | 126.08 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14864 | 126.79 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14864 | 126.92 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14864 | 126.92 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14864 | 126.92 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14864 | 126.92 | P23:500:EES:PERYVL:R7372 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14865 | 126.17 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14865 | 126.39 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14865 | 126.41 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14865 | 126.45 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14866 | 126.53 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14866 | 126.61 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14866 | 126.91 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14867 | 127.05 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14867 | 127.28 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14868 | 126.97 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14868 | 127.02 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14868 | 127.79 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14868 | 128.48 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14869 | 127.04 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14869 | 127.94 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.1487 | 127.42 | P23:500:EAI:NBF_PLEASANT | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.1487 | 130.15 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.1487 | 130.56 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14871 | 126.56 | 547561 NOL443 2 69.0 547566 AND322 2 69.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14871 | 126.85 | 547561 NOL443 2 69.0 547610 NOL435 2 69.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14871 | 129.81 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14873 | 126.87 | 506952 CENTRTN5 161 506980 SHIPERD5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14875 | 127.46 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14877 | 128.5 | P12:345:OKGE:BKRBKR400:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14883 | 130.85 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14884 | 126.99 | P23:500:EES-EAI:MABELV:B5918:_1:: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14888 | 131.13 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14888 | 131.59 | P42:345:OKGE:SB_OPKY7388:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14888 | 131.6 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14888 | 131.6 | P42:345:OKGE:SB_OPKY7319:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14888 | 133.45 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14888 | 134.44 | Potential P4 Event - POI 560053_1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14888 | 134.45 | Potential P4 Event - POI 560053_2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14888 | 134.46 | Potential P4 Event - POI 560053_0 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14888 | 138.33 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.149 | 130.45 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14917 | 127.18 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14917 | 127.18 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14918 | 139.66 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14925 | 139.67 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14925 | 139.67 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14928 | 136.38 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14928 | 139.27 | Potential P4 Event - POI 773480_2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14928 | 139.29 | Potential P4 Event - POI 773480_1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14928 | 139.31 | Potential P4 Event - POI 773480_0 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14928 | 141.9 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14928 | 141.9 | Potential P4 Event - POI 532793_13 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14928 | 141.9 | Potential P4 Event - POI 532793_16 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14928 | 142.34 | Potential P4 Event - POI 532793_18 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14932 | 129.34 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14932 | 130.65 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14932 | 132.65 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14939 | 127.45 | P12:500:OKGE-EESAR:OKGE-EESEAI:BKRBKR317::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14939 | 127.45 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14944 | 128.15 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.14965 | 133.02 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.15121 | 137.3 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.15186 | 138.84 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.15188 | 134.13 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.15276 | 138.14 | 512650 GRDA1 7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.15276 | 143.36 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.15647 | 141.69 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.17074 | 136.91 | 512654 PENSA 5 161 3WXFMR PENAUTO1 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.34275 | 145.23 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 0.36113 | 100.36 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 113.23 | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-028 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 133.78 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-038 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.07313 | 100.46 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-038 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.07313 | 100.46 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-038 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.07313 | 100.46 | Potential P4 Event - POI 508359_5 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-038 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.05687 | 112.2 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-038 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.05687 | 112.2 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-038 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.05687 | 112.2 | Potential P4 Event - POI 508359_5 | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-038 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.0642 | 110.16 | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-038 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.0642 | 110.16 | 521157 HUGO 7 345 3WXFMR HUGO 1 1 | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | 335 | 335 | 1 | 111.67 | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | Cumulative Impact | DRYGULCH5 to G23-028-TAP 161 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16273 | 130.49 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16273 | 130.53 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16367 | 129.02 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16367 | 129.15 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16467 | 125.59 | P12:345:WERE:NRSS-N345-345:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16473 | 125.28 | P12:345:WERE:CANR-G17-345:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16473 | 125.31 | P23:345:WERE:CANR-BKRS:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16526 | 134.01 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16552 | 126.5 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16552 | 126.5 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16557 | 124.32 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16557 | 124.41 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16557 | 124.65 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16561 | 124.39 | P23:345:AEPW:NES CB 3417B NBTB:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16561 | 124.39 | P41:345:AEPW:NES CB 3417B NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16571 | 123.6 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16578 | 123.99 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16578 | 124 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16579 | 126.49 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.1658 | 122.91 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.1658 | 124.41 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.1658 | 124.49 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16581 | 122.91 | 659348 LC_CT1-3-BE7 115 659349 LC_SWY.N-BE7 115 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16581 | 122.94 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16581 | 123.17 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16581 | 123.17 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16581 | 123.17 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16581 | 125.59 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16581 | 127.89 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16581 | 127.89 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16582 | 123.08 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16582 | 123.23 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16582 | 125.01 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 122.66 | 655846 F9______-MK7 115 655872 G9TAP___-MK7 115 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 122.93 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 122.96 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 122.96 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 123.03 | P21:161:ALTW:AUTO-SINGLE:LIMECKL15:CLKREACT5:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 123.1 | 672650 NIPAWIN 4 230 672351 NIPAWIN 2G 13.8 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 123.14 | 773481 GEN-2023-075 345 773482 G23-075XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 123.14 | 773488 G23-075XFMRH 345 773485 G23-075XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 123.2 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 123.24 | GEN-2023-231_POI_776600_Generator_outage | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 123.24 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 123.41 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 123.52 | GEN-2023-075_POI_773480_Generator_outage | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 123.53 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 123.53 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 123.61 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 123.64 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 123.64 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 123.64 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 123.64 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 123.73 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 123.76 | P11:20:AMMO:1LAB G1:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 123.9 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 123.92 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 123.92 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 123.95 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 123.95 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 123.95 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 123.95 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 123.98 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 124.03 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 124.06 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 124.06 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 124.13 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 124.22 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 124.22 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 124.28 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 124.29 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 124.31 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 124.38 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 124.38 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 124.59 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 124.63 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 125.09 | 547501 RIV453 5 161 547643 R13G167 13.8 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 125.3 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16583 | 125.4 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16584 | 123.05 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16584 | 123.81 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16584 | 123.96 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16584 | 123.96 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16584 | 123.96 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16584 | 123.96 | P23:500:EES:PERYVL:R7372 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16585 | 123.14 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16585 | 123.4 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16585 | 123.42 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16585 | 123.46 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16586 | 123.55 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16586 | 123.63 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16586 | 123.96 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16587 | 124.12 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16587 | 124.34 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16587 | 124.9 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16587 | 125.65 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16588 | 124.02 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16588 | 124.08 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16589 | 124.11 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16589 | 125.06 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16589 | 127.45 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16589 | 127.88 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.1659 | 124.48 | P23:500:EAI:NBF_PLEASANT | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.1659 | 127.2 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16591 | 123.84 | 506952 CENTRTN5 161 506980 SHIPERD5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16594 | 124.49 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16596 | 125.74 | P12:345:OKGE:BKRBKR400:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16599 | 127.86 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16603 | 124.02 | P23:500:EES-EAI:MABELV:B5918:_1:: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16605 | 128.69 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16605 | 129.2 | P42:345:OKGE:SB_OPKY7388:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16605 | 129.21 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16605 | 129.21 | P42:345:OKGE:SB_OPKY7319:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16605 | 131.26 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16605 | 132.36 | Potential P4 Event - POI 560053_1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16605 | 132.38 | Potential P4 Event - POI 560053_2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16605 | 132.39 | Potential P4 Event - POI 560053_0 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16605 | 136.66 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16614 | 138.13 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16615 | 128.17 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16622 | 138.13 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16622 | 138.13 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16629 | 134.61 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16629 | 137.83 | Potential P4 Event - POI 773480_2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16629 | 137.84 | Potential P4 Event - POI 773480_1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16629 | 137.86 | Potential P4 Event - POI 773480_0 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16629 | 140.73 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16629 | 140.73 | Potential P4 Event - POI 532793_16 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16629 | 140.74 | Potential P4 Event - POI 532793_13 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16629 | 141.23 | Potential P4 Event - POI 532793_18 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.1663 | 124.17 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.1663 | 124.17 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16636 | 126.52 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16636 | 127.92 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16636 | 130 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16654 | 124.52 | P12:500:OKGE-EESAR:OKGE-EESEAI:BKRBKR317::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16654 | 124.52 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16654 | 130.65 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16663 | 125.57 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.1682 | 135.09 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16832 | 124.78 | 547579 COM381T2 69.0 547590 QUA377 2 69.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16832 | 125.22 | 547579 COM381T2 69.0 547583 FRL363 2 69.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16858 | 136.38 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16866 | 131.36 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.16926 | 140.99 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.17288 | 139.69 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.17601 | 129.16 | 512632 AFTON 5 161 3WXFMR AFTAUTO1 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.17675 | 139.35 | 512633 AFTON 2 69.0 512708 FAIRTAP2 69.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.1806 | 128.94 | 512654 PENSA 5 161 3WXFMR PENAUTO1 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.30765 | 141.88 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16237 | 116.92 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16237 | 116.95 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1644 | 112.44 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16473 | 110.57 | P12:345:WERE:NRSS-N345-345:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1648 | 110.25 | P23:345:WERE:CANR-BKRS:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16507 | 109.96 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16524 | 125.42 | 510417 VINTAJC4 138 547486 HOC404 4 138 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16524 | 125.42 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1658 | 112.31 | P12:161:AEPW-EMDE:FLINTCR5:739952::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16582 | 109.19 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16586 | 109.13 | P23:345:AEPW:NES CB 3417B NBTB:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16586 | 109.13 | P41:345:AEPW:NES CB 3417B NBTB+FAULT:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16587 | 110.09 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16587 | 110.09 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1659 | 108.37 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1659 | 108.45 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16598 | 108.08 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16607 | 108.41 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16607 | 108.43 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16608 | 112.03 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16609 | 107.19 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16609 | 109.24 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1661 | 107.23 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1661 | 107.51 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1661 | 107.52 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1661 | 110.55 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1661 | 113.46 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1661 | 113.46 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16611 | 107.12 | 655841 ARNEGARD-MK7 115 659346 LC_SWY.S-BE7 115 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16611 | 107.18 | 659348 LC_CT1-3-BE7 115 659349 LC_SWY.N-BE7 115 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16611 | 107.44 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 107.26 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 107.26 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 107.33 | P21:161:ALTW:AUTO-SINGLE:LIMECKL15:CLKREACT5:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 107.35 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 107.43 | 672650 NIPAWIN 4 230 672350 NIPAWIN 1G 13.8 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 107.51 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 107.54 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 107.56 | 773481 GEN-2023-075 345 773482 G23-075XFMR1 34.5 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 107.56 | 773488 G23-075XFMRH 345 773485 G23-075XFMR2 34.5 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 107.6 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 107.63 | GEN-2023-231_POI_776600_Generator_outage | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 107.68 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 107.97 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 107.98 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 107.98 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 108.06 | P11:20:AMMO:1LAB G1:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 108.11 | GEN-2023-075_POI_773480_Generator_outage | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 108.13 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 108.13 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 108.14 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 108.14 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 108.2 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 108.27 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 108.42 | P23:345:XEL:8N8 MNN | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 108.47 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 108.47 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 108.47 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 108.47 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 108.47 | P23:345:XEL:8N22 SHC | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 108.48 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 108.48 | P23:345:XEL:8N17 SHC | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 108.57 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 108.67 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 108.67 | P23:345:MEC:CBEC 908 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 108.71 | 773480 G23-075-TAP 345 773481 GEN-2023-075 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 108.76 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 108.78 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 108.87 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 108.88 | P23:345:MEC:CBEC 905 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 108.89 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 109 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 109.07 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 109.32 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 109.35 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 109.41 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 109.66 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 109.77 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 109.98 | 547501 RIV453 5 161 547643 R13G167 13.8 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16612 | 110.6 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16613 | 107.2 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16613 | 108.1 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16613 | 108.21 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16613 | 108.38 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16613 | 108.38 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16613 | 108.38 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16613 | 108.38 | P23:500:EES:PERYVL:R7372 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16614 | 107.39 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16614 | 107.41 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16615 | 107.76 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16615 | 107.78 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16615 | 107.83 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16615 | 107.91 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16615 | 108.01 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16616 | 108.36 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16616 | 108.82 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16617 | 108.31 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16617 | 108.37 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16617 | 108.52 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16617 | 108.8 | P12:500-161:EES-EAI:M:NEW_MAD:PORTGV:WMPEHV:8BHAMSTE:HATI_S:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16617 | 108.95 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16617 | 109.42 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16617 | 110.3 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16618 | 108.49 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16618 | 112.06 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16619 | 109.57 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16619 | 112.52 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.1662 | 112.28 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16622 | 108.63 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16627 | 110.53 | P12:345:OKGE:BKRBKR400:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16634 | 108.43 | P23:500:EES-EAI:MABELV:B5918:_1:: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16637 | 114.12 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16637 | 114.94 | P42:345:OKGE:SB_OPKY7388:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16637 | 114.96 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16637 | 114.96 | P42:345:OKGE:SB_OPKY7319:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16637 | 117.16 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16637 | 118.95 | Potential P4 Event - POI 560053_1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16637 | 118.97 | Potential P4 Event - POI 560053_2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16637 | 118.99 | Potential P4 Event - POI 560053_0 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16637 | 123.58 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16649 | 125.95 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16651 | 113.82 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16658 | 125.89 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16658 | 125.89 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16659 | 110.5 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16659 | 112.16 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16659 | 113.51 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16661 | 108.54 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16661 | 108.54 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16666 | 121.64 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16666 | 125.79 | Potential P4 Event - POI 773480_1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16666 | 125.82 | Potential P4 Event - POI 773480_0 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16666 | 125.83 | Potential P4 Event - POI 773480_2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16666 | 128.99 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16666 | 128.99 | Potential P4 Event - POI 532793_13 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16666 | 128.99 | Potential P4 Event - POI 532793_16 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16666 | 129.62 | Potential P4 Event - POI 532793_18 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16677 | 114.47 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16687 | 108.94 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16805 | 113.84 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16869 | 120.84 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16874 | 120.59 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16903 | 116.38 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.16931 | 124.82 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.17052 | 109.89 | 512632 AFTON 5 161 3WXFMR AFTAUTO1 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.17199 | 111.91 | 547579 COM381T2 69.0 547590 QUA377 2 69.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.17199 | 113.04 | 547579 COM381T2 69.0 547583 FRL363 2 69.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.17357 | 121.9 | 300852 2MIAETP 69.0 512630 MIAMI 2 69.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.17382 | 126.44 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.30516 | 127.14 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.17982 | 143.86 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.17982 | 143.98 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.1802 | 141.47 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.1802 | 141.52 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18214 | 136.56 | P12:345:WERE:NRSS-N345-345:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.1822 | 136.25 | P12:345:WERE:CANR-G17-345:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.1822 | 136.28 | P23:345:WERE:CANR-BKRS:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18242 | 136.11 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18294 | 140.66 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18296 | 137.78 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18296 | 137.78 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18303 | 135.35 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18303 | 135.45 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18303 | 135.67 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18307 | 135.39 | P23:345:AEPW:NES CB 3417B NBTB:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18307 | 135.39 | P41:345:AEPW:NES CB 3417B NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18317 | 134.58 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18324 | 134.97 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18324 | 134.99 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18325 | 137.44 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18326 | 133.89 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18326 | 135.45 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18327 | 133.93 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18327 | 135.48 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18328 | 133.89 | 659348 LC_CT1-3-BE7 115 659349 LC_SWY.N-BE7 115 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18328 | 134.15 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18328 | 134.15 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18328 | 134.16 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18328 | 136.06 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18328 | 136.59 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18328 | 138.9 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18328 | 138.9 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 133.64 | 655846 F9______-MK7 115 655872 G9TAP___-MK7 115 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 133.91 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 133.94 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 133.95 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 134.02 | P21:161:ALTW:AUTO-SINGLE:LIMECKL15:CLKREACT5:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 134.07 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 134.09 | 672650 NIPAWIN 4 230 672351 NIPAWIN 2G 13.8 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 134.12 | 773481 GEN-2023-075 345 773482 G23-075XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 134.12 | 773488 G23-075XFMRH 345 773485 G23-075XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 134.19 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 134.22 | GEN-2023-231_POI_776600_Generator_outage | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 134.22 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 134.23 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 134.39 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 134.5 | GEN-2023-075_POI_773480_Generator_outage | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 134.52 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 134.52 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 134.62 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 134.63 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 134.63 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 134.63 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 134.63 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 134.72 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 134.75 | P11:20:AMMO:1LAB G1:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 134.9 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 134.91 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 134.91 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 134.94 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 134.94 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 134.94 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 134.95 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 134.97 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 135.02 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 135.05 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 135.05 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 135.12 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 135.21 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 135.22 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 135.28 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 135.31 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 135.33 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 135.37 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 135.38 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 135.58 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 135.63 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 136.08 | 547501 RIV453 5 161 547643 R13G167 13.8 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 136.32 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18329 | 136.42 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.1833 | 134.03 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.1833 | 134.81 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.1833 | 134.96 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.1833 | 134.96 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.1833 | 134.96 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.1833 | 134.96 | P23:500:EES:PERYVL:R7372 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18331 | 134.12 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18331 | 134.37 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18331 | 134.39 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18331 | 134.43 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18332 | 134.53 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18332 | 134.62 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18332 | 134.94 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18333 | 135.1 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18333 | 135.35 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18333 | 136.67 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18334 | 134.56 | 547561 NOL443 2 69.0 547566 AND322 2 69.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18334 | 134.88 | 547561 NOL443 2 69.0 547610 NOL435 2 69.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18334 | 135.01 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18334 | 135.06 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18334 | 135.92 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18335 | 135.09 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18335 | 136.08 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18335 | 138.53 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18336 | 135.51 | P23:500:EAI:NBF_PLEASANT | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18336 | 138.16 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18336 | 138.97 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18338 | 134.9 | 506952 CENTRTN5 161 506980 SHIPERD5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.1834 | 135.55 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18342 | 136.71 | P12:345:OKGE:BKRBKR400:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18347 | 139.26 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18349 | 135.03 | P23:500:EES-EAI:MABELV:B5918:_1:: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18351 | 139.62 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18351 | 140.13 | P42:345:OKGE:SB_OPKY7388:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18351 | 140.14 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18351 | 140.14 | P42:345:OKGE:SB_OPKY7319:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18351 | 142.19 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18351 | 143.28 | Potential P4 Event - POI 560053_1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18351 | 143.3 | Potential P4 Event - POI 560053_2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18351 | 143.31 | Potential P4 Event - POI 560053_0 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18351 | 147.58 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18358 | 138.86 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.1836 | 149.07 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18367 | 149.09 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18367 | 149.09 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18374 | 145.44 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18374 | 148.65 | Potential P4 Event - POI 773480_2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18374 | 148.66 | Potential P4 Event - POI 773480_1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18374 | 148.69 | Potential P4 Event - POI 773480_0 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18374 | 151.53 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18374 | 151.53 | Potential P4 Event - POI 532793_16 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18374 | 151.54 | Potential P4 Event - POI 532793_13 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18374 | 152.03 | Potential P4 Event - POI 532793_18 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.1838 | 135.24 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.1838 | 135.24 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18384 | 137.64 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18384 | 139.09 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18384 | 141.28 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18401 | 141.71 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18402 | 135.54 | P12:500:OKGE-EESAR:OKGE-EESEAI:BKRBKR317::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18402 | 135.54 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18403 | 136.33 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18573 | 146.44 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.1862 | 148.15 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18632 | 142.94 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18694 | 147.38 | 512650 GRDA1 7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.18694 | 153.15 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.1906 | 151.32 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.21149 | 146.05 | 512654 PENSA 5 161 3WXFMR PENAUTO1 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.34275 | 155.24 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512633 AFTON 2 69.0 512708 FAIRTAP2 69.0 1 | 72 | 72 | 0.06261 | 199 | P21:161:GRDA:MIAMI5-AFTON5:::HV: | Cumulative Impact | AFTON2 to FAIRTAP2 69 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.17982 | 134.93 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.17982 | 135.05 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.1802 | 132.8 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.1802 | 132.84 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18214 | 128.37 | P12:345:WERE:NRSS-N345-345:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.1822 | 128.09 | P12:345:WERE:CANR-G17-345:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.1822 | 128.12 | P23:345:WERE:CANR-BKRS:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18242 | 127.97 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18294 | 132.05 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18296 | 129.47 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18296 | 129.48 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18303 | 127.28 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18303 | 127.37 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18303 | 127.58 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18307 | 127.3 | P23:345:AEPW:NES CB 3417B NBTB:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18307 | 127.3 | P41:345:AEPW:NES CB 3417B NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18317 | 126.58 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18324 | 126.93 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18324 | 126.95 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18325 | 129.16 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18326 | 125.96 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18326 | 127.37 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18327 | 125.99 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18327 | 127.39 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18328 | 125.96 | 659348 LC_CT1-3-BE7 115 659349 LC_SWY.N-BE7 115 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18328 | 126.19 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18328 | 126.2 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18328 | 126.2 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18328 | 127.91 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18328 | 128.4 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18328 | 130.5 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18328 | 130.5 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 125.72 | 655845 GRDNCRK2-MK7 115 655879 OASIS___-MK7 115 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 125.98 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 126 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 126.01 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 126.07 | P21:161:ALTW:AUTO-SINGLE:LIMECKL15:CLKREACT5:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 126.12 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 126.13 | 672650 NIPAWIN 4 230 672350 NIPAWIN 1G 13.8 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 126.17 | 773481 GEN-2023-075 345 773482 G23-075XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 126.17 | 773488 G23-075XFMRH 345 773485 G23-075XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 126.23 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 126.25 | GEN-2023-231_POI_776600_Generator_outage | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 126.26 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 126.27 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 126.41 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 126.51 | GEN-2023-075_POI_773480_Generator_outage | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 126.52 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 126.53 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 126.61 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 126.62 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 126.62 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 126.63 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 126.63 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 126.7 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 126.74 | P11:20:AMMO:1LAB G1:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 126.86 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 126.88 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 126.88 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 126.9 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 126.9 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 126.91 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 126.91 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 126.93 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 126.98 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 127 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 127 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 127.07 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 127.15 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 127.15 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 127.22 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 127.24 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 127.27 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 127.29 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 127.3 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 127.48 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 127.52 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 127.94 | 547501 RIV453 5 161 547643 R13G167 13.8 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 128.16 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18329 | 128.25 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.1833 | 126.08 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.1833 | 126.79 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.1833 | 126.92 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.1833 | 126.92 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.1833 | 126.92 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.1833 | 126.92 | P23:500:EES:PERYVL:R7372 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18331 | 126.17 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18331 | 126.39 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18331 | 126.41 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18331 | 126.45 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18332 | 126.53 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18332 | 126.61 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18332 | 126.91 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18333 | 127.05 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18333 | 127.28 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18333 | 128.48 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18334 | 126.56 | 547561 NOL443 2 69.0 547566 AND322 2 69.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18334 | 126.85 | 547561 NOL443 2 69.0 547610 NOL435 2 69.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18334 | 126.97 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18334 | 127.02 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18334 | 127.79 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18335 | 127.04 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18335 | 127.94 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18335 | 130.15 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18336 | 127.42 | P23:500:EAI:NBF_PLEASANT | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18336 | 129.81 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18336 | 130.56 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18338 | 126.87 | 506952 CENTRTN5 161 506980 SHIPERD5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.1834 | 127.46 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18342 | 128.5 | P12:345:OKGE:BKRBKR400:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18347 | 130.85 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18349 | 126.99 | P23:500:EES-EAI:MABELV:B5918:_1:: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18351 | 131.13 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18351 | 131.59 | P42:345:OKGE:SB_OPKY7388:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18351 | 131.6 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18351 | 131.6 | P42:345:OKGE:SB_OPKY7319:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18351 | 133.45 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18351 | 134.44 | Potential P4 Event - POI 560053_1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18351 | 134.45 | Potential P4 Event - POI 560053_2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18351 | 134.46 | Potential P4 Event - POI 560053_0 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18351 | 138.33 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18358 | 130.45 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.1836 | 139.66 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18367 | 139.67 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18367 | 139.67 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18374 | 136.38 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18374 | 139.27 | Potential P4 Event - POI 773480_2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18374 | 139.29 | Potential P4 Event - POI 773480_1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18374 | 139.31 | Potential P4 Event - POI 773480_0 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18374 | 141.9 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18374 | 141.9 | Potential P4 Event - POI 532793_13 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18374 | 141.9 | Potential P4 Event - POI 532793_16 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18374 | 142.34 | Potential P4 Event - POI 532793_18 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.1838 | 127.18 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.1838 | 127.18 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18384 | 129.34 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18384 | 130.65 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18384 | 132.65 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18401 | 133.02 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18402 | 127.45 | P12:500:OKGE-EESAR:OKGE-EESEAI:BKRBKR317::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18402 | 127.45 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18403 | 128.15 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18573 | 137.3 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.1862 | 138.84 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18632 | 134.13 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18694 | 138.14 | 512650 GRDA1 7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.18694 | 143.36 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.1906 | 141.69 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.21149 | 136.91 | 512654 PENSA 5 161 3WXFMR PENAUTO1 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.34275 | 145.23 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 0.47548 | 100.36 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 113.23 | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-049 | FROM->TO | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | 1 | 133.78 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.0602 | 130.49 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.0602 | 130.53 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06072 | 125.59 | P12:345:WERE:NRSS-N345-345:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06078 | 125.28 | P12:345:WERE:CANR-G17-345:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06079 | 125.31 | P23:345:WERE:CANR-BKRS:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06104 | 141.88 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06119 | 129.02 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06119 | 129.15 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.0615 | 124.65 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06154 | 124.32 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06154 | 124.41 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06162 | 124.39 | P23:345:AEPW:NES CB 3417B NBTB:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06162 | 124.39 | P41:345:AEPW:NES CB 3417B NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06164 | 123.6 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06172 | 123.99 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06172 | 124 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06173 | 122.91 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06173 | 126.49 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06174 | 122.94 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06174 | 124.49 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06175 | 122.91 | 659348 LC_CT1-3-BE7 115 659349 LC_SWY.N-BE7 115 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06175 | 123.17 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06175 | 123.17 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06175 | 123.17 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06175 | 125.59 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06175 | 127.89 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06175 | 127.89 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 122.66 | 655846 F9______-MK7 115 655872 G9TAP___-MK7 115 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 122.93 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 122.96 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 122.96 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 123.03 | P21:161:ALTW:AUTO-SINGLE:LIMECKL15:CLKREACT5:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 123.08 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 123.1 | 672650 NIPAWIN 4 230 672351 NIPAWIN 2G 13.8 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 123.14 | 773481 GEN-2023-075 345 773482 G23-075XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 123.14 | 773488 G23-075XFMRH 345 773485 G23-075XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 123.2 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 123.23 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 123.24 | GEN-2023-231_POI_776600_Generator_outage | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 123.24 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 123.41 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 123.52 | GEN-2023-075_POI_773480_Generator_outage | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 123.53 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 123.53 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 123.61 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 123.64 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 123.64 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 123.64 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 123.64 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 123.73 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 123.76 | P11:20:AMMO:1LAB G1:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 123.9 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 123.92 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 123.92 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 123.95 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 123.95 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 123.95 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 123.95 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 123.98 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 124.03 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 124.06 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 124.06 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 124.13 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 124.22 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 124.22 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 124.28 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 124.29 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 124.31 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 124.38 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 124.38 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 124.59 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 124.63 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 125.09 | 547501 RIV453 5 161 547643 R13G167 13.8 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 125.3 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06176 | 125.4 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06177 | 123.05 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06177 | 123.81 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06177 | 123.96 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06177 | 123.96 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06177 | 123.96 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06177 | 123.96 | P23:500:EES:PERYVL:R7372 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06178 | 123.14 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06179 | 123.4 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06179 | 123.42 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06179 | 123.46 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06179 | 123.55 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06179 | 123.63 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06179 | 124.41 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06179 | 125.01 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.0618 | 123.96 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.0618 | 124.34 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06181 | 124.02 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06181 | 124.08 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06181 | 124.12 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06181 | 124.9 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06182 | 124.11 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06182 | 125.65 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06183 | 125.06 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06184 | 124.48 | P23:500:EAI:NBF_PLEASANT | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06184 | 127.45 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06185 | 127.88 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06187 | 123.84 | 506952 CENTRTN5 161 506980 SHIPERD5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06187 | 127.2 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06191 | 124.49 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06193 | 125.74 | P12:345:OKGE:BKRBKR400:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06196 | 127.86 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06198 | 124.02 | P23:500:EES-EAI:MABELV:B5918:_1:: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06208 | 128.69 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06208 | 129.2 | P42:345:OKGE:SB_OPKY7388:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06208 | 129.21 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06208 | 129.21 | P42:345:OKGE:SB_OPKY7319:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06208 | 131.26 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06208 | 132.36 | Potential P4 Event - POI 560053_1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06208 | 132.38 | Potential P4 Event - POI 560053_2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06208 | 132.39 | Potential P4 Event - POI 560053_0 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06208 | 136.66 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06218 | 126.5 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06218 | 126.5 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06229 | 124.17 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06229 | 124.17 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06233 | 128.17 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06257 | 124.52 | P12:500:OKGE-EESAR:OKGE-EESEAI:BKRBKR317::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06257 | 124.52 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06282 | 138.13 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06285 | 134.61 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06285 | 137.83 | Potential P4 Event - POI 773480_2 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06285 | 137.84 | Potential P4 Event - POI 773480_1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06285 | 137.86 | Potential P4 Event - POI 773480_0 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06285 | 140.73 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06285 | 140.73 | Potential P4 Event - POI 532793_16 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06285 | 140.74 | Potential P4 Event - POI 532793_13 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06285 | 141.23 | Potential P4 Event - POI 532793_18 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06286 | 126.52 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06286 | 127.92 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06286 | 130 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06291 | 124.78 | 547579 COM381T2 69.0 547590 QUA377 2 69.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06291 | 125.22 | 547579 COM381T2 69.0 547583 FRL363 2 69.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06291 | 138.13 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06291 | 138.13 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06302 | 125.57 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06302 | 134.01 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06386 | 130.65 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06421 | 129.16 | 512632 AFTON 5 161 3WXFMR AFTAUTO1 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06477 | 135.09 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06496 | 131.36 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06502 | 136.38 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06542 | 140.99 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06555 | 128.94 | 512654 PENSA 5 161 3WXFMR PENAUTO1 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.06721 | 139.35 | 512633 AFTON 2 69.0 512708 FAIRTAP2 69.0 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 223 | 223 | 0.07014 | 139.69 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06272 | 116.92 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06272 | 116.95 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06336 | 110.57 | P12:345:WERE:NRSS-N345-345:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06343 | 110.25 | P23:345:WERE:CANR-BKRS:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06391 | 127.14 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06408 | 109.96 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06415 | 112.44 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0643 | 109.19 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06442 | 108.37 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06442 | 108.45 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06444 | 109.13 | P23:345:AEPW:NES CB 3417B NBTB:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06444 | 109.13 | P41:345:AEPW:NES CB 3417B NBTB+FAULT:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06447 | 108.08 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06456 | 108.41 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06456 | 108.43 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06457 | 112.03 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06458 | 107.19 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06458 | 109.24 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06459 | 107.18 | 659348 LC_CT1-3-BE7 115 659349 LC_SWY.N-BE7 115 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06459 | 107.23 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06459 | 107.51 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06459 | 107.52 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06459 | 110.55 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06459 | 113.46 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06459 | 113.46 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 107.12 | 655841 ARNEGARD-MK7 115 659346 LC_SWY.S-BE7 115 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0646 | 107.44 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 107.2 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 107.26 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 107.26 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 107.33 | P21:161:ALTW:AUTO-SINGLE:LIMECKL15:CLKREACT5:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 107.35 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 107.43 | 672650 NIPAWIN 4 230 672350 NIPAWIN 1G 13.8 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 107.51 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 107.54 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 107.56 | 773481 GEN-2023-075 345 773482 G23-075XFMR1 34.5 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 107.56 | 773488 G23-075XFMRH 345 773485 G23-075XFMR2 34.5 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 107.6 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 107.63 | GEN-2023-231_POI_776600_Generator_outage | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 107.68 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 107.97 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 107.98 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 107.98 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 108.06 | P11:20:AMMO:1LAB G1:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 108.11 | GEN-2023-075_POI_773480_Generator_outage | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 108.13 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 108.13 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 108.14 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 108.14 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 108.2 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 108.27 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 108.42 | P23:345:XEL:8N8 MNN | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 108.47 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 108.47 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 108.47 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 108.47 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 108.47 | P23:345:XEL:8N22 SHC | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 108.48 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 108.48 | P23:345:XEL:8N17 SHC | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 108.57 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 108.67 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 108.67 | P23:345:MEC:CBEC 908 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 108.71 | 773480 G23-075-TAP 345 773481 GEN-2023-075 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 108.76 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 108.78 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 108.87 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 108.88 | P23:345:MEC:CBEC 905 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 108.89 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 109 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 109.07 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 109.35 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 109.41 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 109.66 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 109.77 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 109.98 | 547501 RIV453 5 161 547643 R13G167 13.8 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06461 | 110.6 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06462 | 108.1 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06462 | 108.21 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06462 | 108.38 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06462 | 108.38 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06462 | 108.38 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06462 | 108.38 | P23:500:EES:PERYVL:R7372 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06463 | 107.39 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06463 | 107.41 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06464 | 107.76 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06464 | 107.78 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06464 | 107.83 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06464 | 109.32 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06465 | 107.91 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06465 | 108.01 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06465 | 108.36 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06466 | 108.31 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06466 | 108.37 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06466 | 108.52 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06466 | 108.8 | P12:500-161:EES-EAI:M:NEW_MAD:PORTGV:WMPEHV:8BHAMSTE:HATI_S:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06466 | 108.82 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06467 | 108.95 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06467 | 109.42 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06467 | 110.3 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06468 | 108.49 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06469 | 109.57 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0647 | 112.06 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0647 | 112.52 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06473 | 112.28 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06474 | 108.63 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0648 | 110.53 | P12:345:OKGE:BKRBKR400:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06485 | 108.43 | P23:500:EES-EAI:MABELV:B5918:_1:: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06495 | 110.09 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06495 | 110.09 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06498 | 114.12 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06498 | 114.94 | P42:345:OKGE:SB_OPKY7388:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06498 | 114.96 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06498 | 114.96 | P42:345:OKGE:SB_OPKY7319:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06498 | 117.16 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06498 | 118.95 | Potential P4 Event - POI 560053_1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06498 | 118.97 | Potential P4 Event - POI 560053_2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06498 | 118.99 | Potential P4 Event - POI 560053_0 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06498 | 123.58 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06512 | 112.31 | P12:161:AEPW-EMDE:FLINTCR5:739952::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06516 | 108.54 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06516 | 108.54 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06529 | 113.82 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06546 | 108.94 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06557 | 110.5 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06557 | 112.16 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06557 | 113.51 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06567 | 109.89 | 512632 AFTON 5 161 3WXFMR AFTAUTO1 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06584 | 125.95 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06589 | 121.64 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06589 | 125.79 | Potential P4 Event - POI 773480_1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06589 | 125.82 | Potential P4 Event - POI 773480_0 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06589 | 125.83 | Potential P4 Event - POI 773480_2 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06589 | 128.99 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06589 | 128.99 | Potential P4 Event - POI 532793_13 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06589 | 128.99 | Potential P4 Event - POI 532793_16 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06589 | 129.62 | Potential P4 Event - POI 532793_18 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06595 | 125.89 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06595 | 125.89 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06652 | 114.47 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06655 | 125.42 | 510417 VINTAJC4 138 547486 HOC404 4 138 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06655 | 125.42 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0669 | 121.9 | 300852 2MIAETP 69.0 512630 MIAMI 2 69.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06732 | 111.91 | 547579 COM381T2 69.0 547590 QUA377 2 69.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06732 | 113.04 | 547579 COM381T2 69.0 547583 FRL363 2 69.0 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06764 | 113.84 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.0677 | 120.59 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06787 | 120.84 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06789 | 116.38 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.06801 | 124.82 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 167 | 210 | 0.07375 | 126.44 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | MIAMI to HOC404 5 161kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.0644 | 141.47 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.0644 | 141.52 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06493 | 136.56 | P12:345:WERE:NRSS-N345-345:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06498 | 136.25 | P12:345:WERE:CANR-G17-345:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06499 | 136.28 | P23:345:WERE:CANR-BKRS:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06503 | 143.86 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06503 | 143.98 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06515 | 155.24 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06551 | 136.11 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06569 | 135.67 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06573 | 135.35 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06573 | 135.45 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06581 | 135.39 | P23:345:AEPW:NES CB 3417B NBTB:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06581 | 135.39 | P41:345:AEPW:NES CB 3417B NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06584 | 134.58 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06591 | 134.97 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06591 | 134.99 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06592 | 137.44 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06593 | 133.89 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06593 | 135.48 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06594 | 133.89 | 659348 LC_CT1-3-BE7 115 659349 LC_SWY.N-BE7 115 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06594 | 133.93 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06594 | 134.15 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06594 | 134.15 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06594 | 134.16 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06594 | 136.59 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06594 | 138.9 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06594 | 138.9 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 133.64 | 655846 F9______-MK7 115 655872 G9TAP___-MK7 115 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 133.94 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 133.95 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 134.02 | P21:161:ALTW:AUTO-SINGLE:LIMECKL15:CLKREACT5:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 134.07 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 134.09 | 672650 NIPAWIN 4 230 672351 NIPAWIN 2G 13.8 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 134.12 | 773481 GEN-2023-075 345 773482 G23-075XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 134.12 | 773488 G23-075XFMRH 345 773485 G23-075XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 134.19 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 134.22 | GEN-2023-231_POI_776600_Generator_outage | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 134.22 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 134.23 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 134.39 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 134.5 | GEN-2023-075_POI_773480_Generator_outage | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 134.52 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 134.52 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 134.62 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 134.63 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 134.63 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 134.63 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 134.63 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 134.72 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 134.75 | P11:20:AMMO:1LAB G1:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 134.9 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 134.91 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 134.91 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 134.94 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 134.94 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 134.94 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 134.95 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 134.97 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 135.02 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 135.05 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 135.05 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 135.12 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 135.21 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 135.22 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 135.28 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 135.31 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 135.33 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 135.37 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 135.38 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 135.58 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 135.63 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 136.08 | 547501 RIV453 5 161 547643 R13G167 13.8 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 136.32 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06595 | 136.42 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06596 | 133.91 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06596 | 134.03 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06596 | 134.81 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06596 | 134.96 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06596 | 134.96 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06596 | 134.96 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06596 | 134.96 | P23:500:EES:PERYVL:R7372 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06598 | 134.12 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06598 | 134.37 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06598 | 134.39 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06598 | 134.43 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06598 | 136.06 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06599 | 134.53 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06599 | 134.62 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06599 | 134.94 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06599 | 135.45 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.066 | 135.01 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.066 | 135.06 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.066 | 135.1 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.066 | 135.35 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06601 | 135.92 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06601 | 136.67 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06602 | 135.09 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06603 | 135.51 | P23:500:EAI:NBF_PLEASANT | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06603 | 136.08 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06604 | 138.53 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06604 | 138.97 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06606 | 138.16 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06607 | 134.9 | 506952 CENTRTN5 161 506980 SHIPERD5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06611 | 135.55 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06612 | 136.71 | P12:345:OKGE:BKRBKR400:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06615 | 134.56 | 547561 NOL443 2 69.0 547566 AND322 2 69.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06615 | 134.88 | 547561 NOL443 2 69.0 547610 NOL435 2 69.0 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06616 | 139.26 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06618 | 135.03 | P23:500:EES-EAI:MABELV:B5918:_1:: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06627 | 139.62 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06627 | 140.13 | P42:345:OKGE:SB_OPKY7388:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06627 | 140.14 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06627 | 140.14 | P42:345:OKGE:SB_OPKY7319:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06627 | 142.19 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06627 | 143.28 | Potential P4 Event - POI 560053_1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06627 | 143.3 | Potential P4 Event - POI 560053_2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06627 | 143.31 | Potential P4 Event - POI 560053_0 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06627 | 147.58 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06641 | 137.78 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06641 | 137.78 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06648 | 138.86 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06652 | 135.24 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06652 | 135.24 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06673 | 140.66 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06678 | 135.54 | P12:500:OKGE-EESAR:OKGE-EESEAI:BKRBKR317::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06678 | 135.54 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06701 | 149.07 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06703 | 145.44 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06703 | 148.65 | Potential P4 Event - POI 773480_2 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06703 | 148.66 | Potential P4 Event - POI 773480_1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06703 | 148.69 | Potential P4 Event - POI 773480_0 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06703 | 151.53 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06703 | 151.53 | Potential P4 Event - POI 532793_16 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06703 | 151.54 | Potential P4 Event - POI 532793_13 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06703 | 152.03 | Potential P4 Event - POI 532793_18 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06708 | 149.09 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06708 | 149.09 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06709 | 137.64 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06709 | 139.09 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06709 | 141.28 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06711 | 136.33 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06807 | 141.71 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06905 | 146.44 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06937 | 142.94 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.0694 | 148.15 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06984 | 147.38 | 512650 GRDA1 7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.06984 | 153.15 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.07319 | 146.05 | 512654 PENSA 5 161 3WXFMR PENAUTO1 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 223 | 223 | 0.07465 | 151.32 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.0644 | 132.8 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.0644 | 132.84 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06493 | 128.37 | P12:345:WERE:NRSS-N345-345:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06498 | 128.09 | P12:345:WERE:CANR-G17-345:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06499 | 128.12 | P23:345:WERE:CANR-BKRS:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06503 | 134.93 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06503 | 135.05 | P12:138:AEPW:VINTAJC4:N.E.S.-4::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06515 | 145.23 | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06551 | 127.97 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06569 | 127.58 | 547498 STL439 5 161 547658 S4G439 1 18.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06573 | 127.28 | P12:HV:EES::5HARRISON.E!:5EVERTON RD:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06573 | 127.37 | P12:HV:EES::5ST JOE:5HILLTOP%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06581 | 127.3 | P23:345:AEPW:NES CB 3417B NBTB:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06581 | 127.3 | P41:345:AEPW:NES CB 3417B NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06584 | 126.58 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06591 | 126.93 | P12:345:WERE:SWIS-WGAR-345:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06591 | 126.95 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06592 | 129.16 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06593 | 125.96 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06593 | 127.39 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06594 | 125.96 | 659348 LC_CT1-3-BE7 115 659349 LC_SWY.N-BE7 115 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06594 | 125.99 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06594 | 126.19 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06594 | 126.2 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06594 | 126.2 | P12:EHV:EES::7GRIMES%:CROCKET7:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06594 | 128.4 | 547501 RIV453 5 161 547642 R12G4531 13.8 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06594 | 130.5 | 547469 RIV4525 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06594 | 130.5 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 125.72 | 655845 GRDNCRK2-MK7 115 655879 OASIS___-MK7 115 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 126 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 126.01 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 126.07 | P21:161:ALTW:AUTO-SINGLE:LIMECKL15:CLKREACT5:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 126.12 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 126.13 | 672650 NIPAWIN 4 230 672350 NIPAWIN 1G 13.8 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 126.17 | 773481 GEN-2023-075 345 773482 G23-075XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 126.17 | 773488 G23-075XFMRH 345 773485 G23-075XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 126.23 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 126.25 | GEN-2023-231_POI_776600_Generator_outage | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 126.26 | P12:EHV:EES::8NELSON%:8RICHARD%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 126.27 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 126.41 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 126.51 | GEN-2023-075_POI_773480_Generator_outage | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 126.52 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 126.53 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 126.61 | 515310 QUANXTP5 161 515474 QUANEXS5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 126.62 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 126.62 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 126.63 | 764300 GEN-2020-079 161 775862 G23-194XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 126.63 | GEN-2023-194_POI_764310_Generator_outage | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 126.7 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 126.74 | P11:20:AMMO:1LAB G1:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 126.86 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 126.88 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 126.88 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 126.9 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 126.9 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 126.91 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 126.91 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 126.93 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 126.98 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 127 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 127 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 127.07 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 127.15 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 127.15 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 127.22 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 127.24 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 127.27 | P11:HV:EES::JTEC GEN#2 1:2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 127.29 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 127.3 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 127.48 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 127.52 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 127.94 | 547501 RIV453 5 161 547643 R13G167 13.8 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 128.16 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06595 | 128.25 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06596 | 125.98 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06596 | 126.08 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06596 | 126.79 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06596 | 126.92 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06596 | 126.92 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06596 | 126.92 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06596 | 126.92 | P23:500:EES:PERYVL:R7372 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06598 | 126.17 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06598 | 126.39 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06598 | 126.41 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06598 | 126.45 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06598 | 127.91 | P12:161:EES-EAI:M:DANVL2:DARDNL:DARD_D:RUSL_S:RUSL_E:HILTOP_E:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06599 | 126.53 | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06599 | 126.61 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06599 | 126.91 | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06599 | 127.37 | 301622 5MORGANXF1 161 300045 7MORGAN 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.066 | 126.97 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.066 | 127.02 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.066 | 127.05 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.066 | 127.28 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06601 | 127.79 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06601 | 128.48 | P23:345:WERE:WAVS-BKRS:::EHV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06602 | 127.04 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06603 | 127.42 | P23:500:EAI:NBF_PLEASANT | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06603 | 127.94 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06604 | 130.15 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06604 | 130.56 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06606 | 129.81 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06607 | 126.87 | 506952 CENTRTN5 161 506980 SHIPERD5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06611 | 127.46 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06612 | 128.5 | P12:345:OKGE:BKRBKR400:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06615 | 126.56 | 547561 NOL443 2 69.0 547566 AND322 2 69.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06615 | 126.85 | 547561 NOL443 2 69.0 547610 NOL435 2 69.0 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06616 | 130.85 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06618 | 126.99 | P23:500:EES-EAI:MABELV:B5918:_1:: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06627 | 131.13 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06627 | 131.59 | P42:345:OKGE:SB_OPKY7388:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06627 | 131.6 | P42:345:OKGE:SB_OPKY7308:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06627 | 131.6 | P42:345:OKGE:SB_OPKY7319:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06627 | 133.45 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06627 | 134.44 | Potential P4 Event - POI 560053_1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06627 | 134.45 | Potential P4 Event - POI 560053_2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06627 | 134.46 | Potential P4 Event - POI 560053_0 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06627 | 138.33 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06641 | 129.47 | 503997 SIBLEYRD5 161 547484 DEC392 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06641 | 129.48 | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06648 | 130.45 | P12:138:WERE:DEAR-PSO-138:::HV: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06652 | 127.18 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06652 | 127.18 | 300741 5SPORTSMAN 161 300740 7SPORTSMAN 345 2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06673 | 132.05 | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06678 | 127.45 | P12:500:OKGE-EESAR:OKGE-EESEAI:BKRBKR317::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06678 | 127.45 | P12:EHV:EES::8ANO%:FTSMITH8%:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06701 | 139.66 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06703 | 136.38 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06703 | 139.27 | Potential P4 Event - POI 773480_2 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06703 | 139.29 | Potential P4 Event - POI 773480_1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06703 | 139.31 | Potential P4 Event - POI 773480_0 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06703 | 141.9 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06703 | 141.9 | Potential P4 Event - POI 532793_13 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06703 | 141.9 | Potential P4 Event - POI 532793_16 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06703 | 142.34 | Potential P4 Event - POI 532793_18 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06708 | 139.67 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06708 | 139.67 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06709 | 129.34 | P12:HV:EES::AVOCA 5:BEAVER 5!:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06709 | 130.65 | P12:HV:EES::BEAVER 5!:EROGERS5:1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06709 | 132.65 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06711 | 128.15 | 505486 NEO SPA5 161 547471 NEO184 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06807 | 133.02 | 547471 NEO184 5 161 547496 NOL435 5 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06905 | 137.3 | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06937 | 134.13 | 300741 5SPORTSMAN 161 301348 5CHOTEAU2 161 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.0694 | 138.84 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06984 | 138.14 | 512650 GRDA1 7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.06984 | 143.36 | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.07319 | 136.91 | 512654 PENSA 5 161 3WXFMR PENAUTO1 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-055 | FROM->TO | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 248 | 248 | 0.07465 | 141.69 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-056 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.70399 | 102.3 | P42:345:OKGE:SB_FTTH7386:::: | Cumulative Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-056 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.70605 | 102.35 | P12:345:OKGE:BKRBKR295:::: | Cumulative Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-056 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.70605 | 102.35 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1 | Cumulative Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-056 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.70605 | 102.35 | P41:345:OKGE:SB_MUGE7385:::: | Cumulative Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-056 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.7541 | 110.08 | 515264 TARBY 5 161 515265 SHAD-PT5 161 1 | Cumulative Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-056 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.7541 | 112.62 | 515254 SUNSTCN5 161 515265 SHAD-PT5 161 1 | Cumulative Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-056 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.7541 | 112.88 | P12:161:OKGE-SWPA-WFEC:BKRBKR4:::: | Cumulative Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-056 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.7541 | 113.4 | 505582 RS KERR5 161 515254 SUNSTCN5 161 1 | Cumulative Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.58964 | 109.07 | 509050 KEATCHI4 138 509064 GEORPAC4 138 1 | Cumulative Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.58964 | 110.24 | 509050 KEATCHI4 138 509052 STONWAL4 138 1 | Cumulative Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.58964 | 111.31 | 507793 LEASIDE 4 138 509052 STONWAL4 138 1 | Cumulative Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.6004 | 113.43 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.6004 | 113.43 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.6004 | 113.43 | Potential P4 Event - POI 508359_5 | Cumulative Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.60233 | 104.88 | Potential P4 Event - POI 508563_3 | Cumulative Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.60235 | 104.87 | P42:345:AEPW:PIRKEY CB 13430 NBTB+FAULT:::: | Cumulative Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.60235 | 104.87 | Potential P4 Event - POI 508563_1 | Cumulative Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.60238 | 104.87 | P12:345:AEPW:PIRKEY7:DIANA7::: | Cumulative Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.61206 | 102.53 | P23:500:AEPW-EES:ABF_HTBG-A | Cumulative Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.61681 | 105.32 | P13:345,230:CLEC::DOLHILL::1 | Cumulative Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.61681 | 105.32 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-059 | FROM->TO | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 219 | 219 | 0.61681 | 105.32 | P13:345-230:CLEC:DOLET:5092 | Cumulative Impact | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-064 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.2858 | 102.3 | P42:345:OKGE:SB_FTTH7386:::: | Cumulative Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-064 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.28763 | 102.35 | P12:345:OKGE:BKRBKR295:::: | Cumulative Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-064 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.28763 | 102.35 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1 | Cumulative Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-064 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.28763 | 102.35 | P41:345:OKGE:SB_MUGE7385:::: | Cumulative Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-064 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.51794 | 110.08 | 515264 TARBY 5 161 515265 SHAD-PT5 161 1 | Cumulative Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-064 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.51794 | 112.62 | 515254 SUNSTCN5 161 515265 SHAD-PT5 161 1 | Cumulative Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-064 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.51794 | 112.88 | P12:161:OKGE-SWPA-WFEC:BKRBKR4:::: | Cumulative Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-064 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.51794 | 113.4 | 505582 RS KERR5 161 515254 SUNSTCN5 161 1 | Cumulative Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-069 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.09046 | 100.46 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-069 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.09046 | 100.46 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-069 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.09046 | 100.46 | Potential P4 Event - POI 508359_5 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-069 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.07564 | 112.2 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-069 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.07564 | 112.2 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-069 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.07564 | 112.2 | Potential P4 Event - POI 508359_5 | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-069 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.07771 | 102.7 | P23:345:AEPW:VALLIANT CB 3413A NBTB:::: | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-069 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.07771 | 102.7 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT:::: | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-069 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.07932 | 105.06 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-069 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.1225 | 110.16 | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-069 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.1225 | 110.16 | 521157 HUGO 7 345 3WXFMR HUGO 1 1 | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-088 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.06086 | 110.08 | 515264 TARBY 5 161 515265 SHAD-PT5 161 1 | Cumulative Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-088 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.06086 | 112.62 | 515254 SUNSTCN5 161 515265 SHAD-PT5 161 1 | Cumulative Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-088 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.06086 | 112.88 | P12:161:OKGE-SWPA-WFEC:BKRBKR4:::: | Cumulative Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-088 | FROM->TO | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 335 | 335 | 0.06086 | 113.4 | 505582 RS KERR5 161 515254 SUNSTCN5 161 1 | Cumulative Impact | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-092 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.16103 | 100.46 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-092 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.16103 | 100.46 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-092 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.16103 | 100.46 | Potential P4 Event - POI 508359_5 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-092 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.15121 | 112.2 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-092 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.15121 | 112.2 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-092 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.15121 | 112.2 | Potential P4 Event - POI 508359_5 | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-092 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.26585 | 102.7 | P23:345:AEPW:VALLIANT CB 3413A NBTB:::: | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-092 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.26585 | 102.7 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT:::: | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-092 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.2681 | 105.06 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-092 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.42381 | 110.16 | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-092 | FROM->TO | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 287 | 287 | 0.42381 | 110.16 | 521157 HUGO 7 345 3WXFMR HUGO 1 1 | Cumulative Impact | VALIANT to HUGO 138 kV Ckt 1 Rating Update
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-101 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 435 | 435 | 1 | 108.88 | 523777 WHEELER 6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-101 | FROM->TO | 523777 WHEELER 6 230 774000 G23-101-TAP 230 1 | 439 | 439 | 1 | 108.32 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing WHEELER 6 to G23-101-TAP 230 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-135 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.30537 | 100.46 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-135 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.30537 | 100.46 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-135 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.30537 | 100.46 | Potential P4 Event - POI 508359_5 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-135 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.28415 | 112.2 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-135 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.28415 | 112.2 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-135 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.28415 | 112.2 | Potential P4 Event - POI 508359_5 | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-151 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.07057 | 100.46 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-151 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.07057 | 100.46 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-151 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.07057 | 100.46 | Potential P4 Event - POI 508359_5 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-151 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.09593 | 112.2 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-151 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.09593 | 112.2 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-151 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.09593 | 112.2 | Potential P4 Event - POI 508359_5 | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-174 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.05316 | 100.46 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-174 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.05316 | 100.46 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-174 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.05316 | 100.46 | Potential P4 Event - POI 508359_5 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-177 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.05839 | 100.46 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-177 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.05839 | 100.46 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-177 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.05839 | 100.46 | Potential P4 Event - POI 508359_5 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-211 | FROM->TO | 514803 SOONER 7 345 515576 RANCHRD7 345 1 | 1716 | 1793 | 1 | 100.82 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-211 | FROM->TO | 514803 SOONER 7 345 515576 RANCHRD7 345 1 | 1716 | 1793 | 1 | 100.83 | Potential P4 Event - POI 532794_5 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-211 | FROM->TO | 514803 SOONER 7 345 515576 RANCHRD7 345 1 | 1716 | 1793 | 1 | 100.83 | Potential P4 Event - POI 532794_7 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-211 | FROM->TO | 514803 SOONER 7 345 515576 RANCHRD7 345 1 | 1716 | 1793 | 1 | 100.84 | Potential P4 Event - POI 532794_2 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1793 | 1793 | 1 | 101.81 | P42:345:OKGE:SB_RARD7383:::: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1793 | 1793 | 1 | 102.64 | P12:345:OKGE:BKRBKR357_1:::: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1793 | 1793 | 1 | 102.64 | P42:345:OKGE:SB_SOER7383:::: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1793 | 1793 | 1 | 102.64 | Potential P4 Event - POI 514803_8 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1793 | 1793 | 1 | 102.67 | Potential P4 Event - POI 514803_0 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-211 | FROM->TO | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 1793 | 1793 | 1 | 102.68 | Potential P4 Event - POI 514803_7 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-212 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.24242 | 100.46 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-212 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.24242 | 100.46 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-212 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 1323 | 1393 | 0.24242 | 100.46 | Potential P4 Event - POI 508359_5 | Cumulative Impact | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-212 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.2515 | 112.2 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-212 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.2515 | 112.2 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-212 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.2515 | 112.2 | Potential P4 Event - POI 508359_5 | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-227 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.12091 | 112.2 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-227 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.12091 | 112.2 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 04ALL | 1 | 27WP | GEN-2023-227 | FROM->TO | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 1256 | 1256 | 0.12091 | 112.2 | Potential P4 Event - POI 508359_5 | Cumulative Impact | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03588 | 131.38 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03588 | 104.3 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03588 | 130.19 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 103.1 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.27 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.56 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.93 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03296 | 131.38 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03296 | 104.3 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03296 | 130.19 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 103.1 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.27 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 108.56 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 108.93 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03213 | 131.38 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03213 | 104.3 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03213 | 130.19 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.1 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 143.78 | System-Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 145.95 | System-Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.27 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.56 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.93 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 103.1 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.04932 | 143.78 | System-Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.04932 | 145.95 | System-Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.56 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.93 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03717 | 131.38 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03717 | 104.3 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03717 | 130.19 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 103.1 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 143.78 | System-Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 145.95 | System-Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.03752 | 135.27 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 108.56 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 108.93 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03213 | 131.38 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03213 | 104.3 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03213 | 130.19 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.1 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 143.78 | System-Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 145.95 | System-Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.27 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.56 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.93 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.0352 | 131.38 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0352 | 104.3 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.0352 | 130.19 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 103.1 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.27 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 108.56 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 108.93 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.0389 | 131.38 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0389 | 104.3 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.0389 | 130.19 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 103.1 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 143.78 | System-Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 145.95 | System-Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.27 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 108.56 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 108.93 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03724 | 131.38 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03724 | 104.3 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03724 | 130.19 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 103.1 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03189 | 131.38 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03189 | 104.3 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03189 | 130.19 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 103.1 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 143.78 | System-Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 145.95 | System-Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525454 HALE_CNTY 3 115 525828 TUCO_INT 3 115 1 | 96 | 106 | 0.10906 | 105.75 | System-Intact | TDF Impact | Rebuild the existing HALE_CNTY3 to TUCO3 115 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.56 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.93 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.04113 | 131.38 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.04113 | 104.3 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.04113 | 130.19 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 117.76 | System-Intact | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 119.59 | System-Intact | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 103.1 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 143.78 | System-Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 145.95 | System-Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.03962 | 135.27 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 108.56 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 108.93 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03213 | 131.38 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03213 | 104.3 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03213 | 130.19 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.1 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 143.78 | System-Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 145.95 | System-Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.27 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.56 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.93 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03213 | 131.38 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03213 | 104.3 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03213 | 130.19 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.1 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 143.78 | System-Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 145.95 | System-Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.27 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.56 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.93 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03174 | 131.38 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03174 | 104.3 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03174 | 130.19 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 103.1 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 143.78 | System-Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 145.95 | System-Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.27 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.56 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.93 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03174 | 131.38 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03174 | 104.3 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03174 | 130.19 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 103.1 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 143.78 | System-Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 145.95 | System-Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.27 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.56 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.93 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03213 | 131.38 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03213 | 104.3 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03213 | 130.19 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.1 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 143.78 | System-Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 145.95 | System-Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.27 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.56 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.93 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03242 | 131.38 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03242 | 104.3 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03242 | 130.19 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 103.1 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 143.78 | System-Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 145.95 | System-Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.27 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 108.56 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 108.93 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03604 | 131.38 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03604 | 104.3 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03604 | 130.19 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 103.1 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.27 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 108.56 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 108.93 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.04806 | 103.1 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03219 | 131.38 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03219 | 104.3 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03219 | 130.19 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 103.1 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 143.78 | System-Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 145.95 | System-Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.27 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 108.56 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 108.93 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03438 | 131.38 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03438 | 104.3 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03438 | 130.19 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 103.1 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.27 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 108.56 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 108.93 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03187 | 131.38 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03187 | 104.3 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03187 | 130.19 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 103.1 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 135.27 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 108.56 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10659 | 108.93 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.04273 | 131.38 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.04273 | 104.3 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.04273 | 130.19 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10157 | 103.1 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 143.78 | System-Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 145.95 | System-Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.04335 | 135.27 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 108.56 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10693 | 108.93 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.0419 | 131.38 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0419 | 104.3 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.0419 | 130.19 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09997 | 103.1 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 143.78 | System-Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 145.95 | System-Intact | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.04408 | 135.27 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 108.56 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11676 | 108.93 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 103.1 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03357 | 131.38 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03357 | 104.3 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.03357 | 130.19 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08818 | 103.1 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06184 | 135.27 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 108.56 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09246 | 108.93 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 103.1 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.03578 | 127.14 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03578 | 100.64 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.03578 | 126.02 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 102.38 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06277 | 134.46 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 107.77 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08916 | 108.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.03287 | 127.14 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03287 | 100.64 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.03287 | 126.02 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 102.38 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0614 | 134.46 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 107.77 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10243 | 108.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.03204 | 127.14 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03204 | 100.64 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.03204 | 126.02 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.38 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.01 | System-Intact | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.46 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.77 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07016 | 102.38 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.77 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.03697 | 127.14 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03697 | 100.64 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.03697 | 126.02 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12568 | 102.38 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.03632 | 134.46 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 107.77 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0751 | 108.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.03204 | 127.14 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03204 | 100.64 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.03204 | 126.02 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.38 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.01 | System-Intact | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.46 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.77 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.0351 | 127.14 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0351 | 100.64 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.0351 | 126.02 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 102.38 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07073 | 134.46 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 107.77 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09518 | 108.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.03875 | 127.14 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03875 | 100.64 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.03875 | 126.02 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09827 | 102.38 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.04888 | 134.46 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 107.77 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12378 | 108.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.03718 | 127.14 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03718 | 100.64 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.03718 | 126.02 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06954 | 102.38 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.0318 | 127.14 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0318 | 100.64 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.0318 | 126.02 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08556 | 102.38 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525454 HALE_CNTY 3 115 525828 TUCO_INT 3 115 1 | 96 | 106 | 0.10832 | 104.79 | System-Intact | TDF Impact | Rebuild the existing HALE_CNTY3 to TUCO3 115 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.77 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.04096 | 127.14 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.04096 | 100.64 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.04096 | 126.02 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 117.23 | System-Intact | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 121.1 | System-Intact | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11268 | 102.38 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.03833 | 134.46 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 107.77 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08874 | 108.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.03204 | 127.14 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03204 | 100.64 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.03204 | 126.02 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.38 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.01 | System-Intact | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.46 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.77 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.03204 | 127.14 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03204 | 100.64 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.03204 | 126.02 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.38 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.01 | System-Intact | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.46 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.77 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.03165 | 127.14 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03165 | 100.64 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.03165 | 126.02 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 102.38 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0397 | 100.01 | System-Intact | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.46 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.77 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.03165 | 127.14 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03165 | 100.64 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.03165 | 126.02 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 102.38 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0397 | 100.01 | System-Intact | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.46 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.77 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.03204 | 127.14 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03204 | 100.64 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.03204 | 126.02 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.38 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.01 | System-Intact | TDF Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.46 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.77 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.03233 | 127.14 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03233 | 100.64 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.03233 | 126.02 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 102.38 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.46 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 107.77 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.03593 | 127.14 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03593 | 100.64 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.03593 | 126.02 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 102.38 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.46 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 107.77 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.04845 | 102.38 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.0321 | 127.14 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0321 | 100.64 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.0321 | 126.02 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 102.38 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.46 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 107.77 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.03429 | 127.14 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03429 | 100.64 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.03429 | 126.02 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 102.38 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.46 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 107.77 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.03179 | 127.14 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03179 | 100.64 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.03179 | 126.02 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 102.38 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.46 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 107.77 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.04258 | 127.14 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.04258 | 100.64 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.04258 | 126.02 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 102.38 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.04196 | 134.46 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 107.77 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.04175 | 127.14 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.04175 | 100.64 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.04175 | 126.02 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 102.38 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.04273 | 134.46 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 107.77 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 102.38 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.03349 | 127.14 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.03349 | 100.64 | System-Intact | TDF Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.03349 | 126.02 | System-Intact | TDF Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 102.38 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.46 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 107.77 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 102.38 | System-Intact | TDF Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 139.58 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.26 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.17 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.82 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 139.58 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.26 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.17 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.82 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.58 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.26 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.17 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.82 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.26 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.17 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.82 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.03499 | 139.58 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.26 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.17 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.82 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.58 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.26 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.17 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.82 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 139.58 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.26 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.17 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.82 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.04756 | 139.58 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.26 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.17 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.82 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525454 HALE_CNTY 3 115 525828 TUCO_INT 3 115 1 | 107 | 117 | 0.10829 | 106.11 | System-Intact | TDF Impact | Rebuild the existing HALE_CNTY3 to TUCO3 115 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.26 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.17 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18842 | 109.82 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.037 | 139.58 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 125.26 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.17 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08771 | 126.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07644 | 109.82 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.58 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.26 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.17 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.82 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.58 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.26 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.17 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.82 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.58 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.26 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.17 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.82 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16715 | 139.58 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 125.26 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.17 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16627 | 126.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1449 | 109.82 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.58 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.26 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.17 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.82 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16226 | 139.58 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 125.26 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.17 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16573 | 126.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14443 | 109.82 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06084 | 139.58 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 125.26 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.17 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08734 | 126.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07612 | 109.82 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1723 | 139.58 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 125.26 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.17 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16978 | 126.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14796 | 109.82 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06433 | 139.58 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 125.26 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.17 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09266 | 126.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08075 | 109.82 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05794 | 139.58 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 125.26 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.17 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10475 | 126.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09129 | 109.82 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.04063 | 139.58 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 125.26 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.17 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 126.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08681 | 109.82 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.04141 | 139.58 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 125.26 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.17 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 126.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09559 | 109.82 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06003 | 139.58 | System-Intact | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 125.26 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.17 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09089 | 126.01 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07921 | 109.82 | System-Intact | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21061 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24545 | 154.86 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26476 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31305 | 187.42 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31526 | 183.57 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31526 | 183.59 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31526 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31526 | 195.61 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31601 | 188.13 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24292 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24524 | 155.38 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31273 | 187.81 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31493 | 184.02 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31493 | 184.11 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31493 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31493 | 196.06 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.3157 | 188.56 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20122 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20343 | 100.01 | P11:25:EES:WATERF:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20343 | 100.01 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20343 | 100.01 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20343 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20343 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20343 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20343 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20343 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20343 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20343 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20343 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20343 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20343 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20343 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20489 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20489 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2049 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20505 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20505 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2051 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2051 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20531 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20538 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20542 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20576 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20576 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20652 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20705 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20743 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20744 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20876 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20885 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20901 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20907 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20908 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21075 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21141 | 107.18 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21147 | 106.47 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21147 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21429 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22537 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22663 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28065 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.29595 | 154.86 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38476 | 187.42 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.3849 | 188.13 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38794 | 183.57 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38794 | 183.59 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38794 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38794 | 195.61 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.20793 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25749 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.29569 | 155.38 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38437 | 187.81 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38452 | 188.56 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38754 | 184.02 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38754 | 184.11 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38754 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38754 | 196.06 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 528413 TAYLOR 3 115 528449 W_BENDER 3 115 1 | 143 | 157 | 1 | 135.45 | 528355 MADDOX 3 115 762442 G18-004-TAP 115 1 | TDF Impact | Rebuild the existing TAYLOR3 to W_BENDER3 115 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 162.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 164.73 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 164.73 | Potential P4 Event - POI 527656_11 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20168 | 165.04 | Potential P4 Event - POI 527656_13 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20168 | 165.04 | Potential P4 Event - POI 527656_14 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20192 | 165.64 | Potential P4 Event - POI 527656_0 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.202 | 164.89 | Potential P4 Event - POI 527656_10 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21015 | 109.73 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21015 | 110.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20042 | 124.23 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20447 | 138.42 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 128.24 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 131.95 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 135.41 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 135.88 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 138.79 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 139.6 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 139.63 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 140.37 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 119.52 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 119.53 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29756 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28714 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.01 | P11:25:EES:WATERF:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.01 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.01 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22324 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22435 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22435 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22435 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2245 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2245 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22456 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22456 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22469 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22474 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22595 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22628 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22629 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22646 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22651 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22685 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22685 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22783 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22816 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22825 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22841 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22847 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22848 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2301 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23078 | 107.18 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23083 | 106.47 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23083 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2319 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23285 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24205 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25113 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25198 | 104.54 | Potential P4 Event - POI 527656_13 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2663 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38265 | 154.86 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41996 | 188.13 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4214 | 187.42 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 183.57 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 183.59 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 195.61 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22208 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24432 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38232 | 155.38 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41955 | 188.56 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42097 | 187.81 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 184.02 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 184.11 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 196.06 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20042 | 124.63 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20447 | 141.25 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 130.11 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 134.46 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 137.98 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 138.46 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 141.54 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 142.35 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 142.4 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 143.16 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 118.53 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 120.63 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 120.63 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29756 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28714 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2835 | 113.29 | GEN-2023-237_POI_560022_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35171 | 138.42 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35336 | 128.24 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35336 | 131.95 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35336 | 135.41 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35336 | 135.88 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35336 | 138.79 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35336 | 139.6 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35336 | 139.63 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35336 | 140.37 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35802 | 109.05 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35802 | 109.05 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3582 | 108.48 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3582 | 108.48 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35823 | 108.48 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35823 | 108.65 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35823 | 108.87 | P23:500:EES:PERRYVILLE:R7372::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.39 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.46 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.48 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.64 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.64 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.67 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.67 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.79 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.82 | P13:138:EES:LC:T1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.82 | P13:138:EES:LC:T2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.87 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.89 | P11:EHV:EES::1FRNTR 1!:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.9 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.9 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.92 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.94 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.94 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.99 | P13:230,22:CLEC::G2RODEMR::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.03 | P23:500:EES:PERRYVILLE:R3779::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.04 | P11:18:EES:NINEMI:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.14 | P13:230,22:CLEC::G3MADISN::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.15 | P11:HV:EES::1ISES U1:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.15 | P13:230:EES:NINEMI:AT4 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.16 | P11:EHV:EES::1ISES U2:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.17 | P11:26:EES:NINEMI:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.17 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.17 | P13:230:EES:NINEMI:AT5 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.18 | P11:22:CLEC:RODEMR1:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.18 | P11:26:EES:NINEMI:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.18 | P11:HV:EES::1NMIL U5!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.22 | P12:EHV:EES::8WHT BLUFF%:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.22 | P13:500:EES-EAI:WH_BLF:ST2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.23 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.24 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.26 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.3 | P13:345,24:CLEC::G1DOLHILL::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.37 | P12:EHV:EES::8ANO%:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.4 | P11:22:EES-EAI:ARK_NU:1:D395 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.49 | P11:21:EES:RVB:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.49 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.49 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.49 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.49 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.53 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.53 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.53 | P11:HV:EES::1LEWIS_U3 ST:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.58 | P11:25:EES:WATERF:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.58 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.59 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.69 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.69 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.69 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.75 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.75 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.78 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 110.66 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 110.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 111.04 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 111.24 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 113.28 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35825 | 108.99 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3583 | 108.45 | P13:345:OPPD:NEBCTY1G:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3583 | 108.45 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3583 | 108.45 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3583 | 108.69 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35831 | 108.82 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35832 | 108.76 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35832 | 108.77 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35833 | 108.9 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35833 | 108.9 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35834 | 108.28 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35842 | 108.95 | P23:345:WERE:WICH-345-50:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35843 | 108.98 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35844 | 109.13 | P13:69-138:AEPW:SHAM 2WT:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35844 | 109.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3585 | 108.99 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35859 | 109.44 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35865 | 108.99 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35865 | 109.39 | P23:345:WERE:BUFF-345-534:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35865 | 109.39 | P23:345:WERE:BUFF-345-543:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35895 | 110.1 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35896 | 111.09 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35906 | 110.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35906 | 110.68 | P23:345:SUNC:BU_BRK482:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35913 | 111.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35913 | 111.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35914 | 110.77 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35915 | 111.03 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35916 | 111.04 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35927 | 110.71 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35927 | 110.82 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35959 | 113.28 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35988 | 112.35 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35988 | 112.35 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36015 | 112.1 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36044 | 111.42 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36083 | 116.25 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36123 | 115.8 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36131 | 115.86 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36146 | 116.15 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36146 | 116.15 | Potential P4 Event - POI 531449_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36216 | 117.14 | POI 515800_22 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36216 | 117.29 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36281 | 117.38 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36345 | 121.61 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36345 | 122.52 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36347 | 118.97 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36925 | 119.52 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36925 | 119.53 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36946 | 124.23 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.59362 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30651 | 120.63 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30794 | 111.76 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30794 | 115 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30794 | 118.01 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30794 | 118.42 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30794 | 120.96 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30794 | 121.66 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30794 | 121.68 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30794 | 122.33 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31445 | 101.31 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3148 | 100.92 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31487 | 100.97 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.315 | 101.22 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.315 | 101.22 | Potential P4 Event - POI 531449_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31561 | 102.08 | POI 515800_22 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31561 | 102.22 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31618 | 102.3 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31674 | 105.99 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31674 | 106.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31675 | 103.69 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.32179 | 104.17 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.32179 | 104.17 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.32197 | 108.27 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.57283 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23375 | 102.88 | GEN-2023-237_POI_560022_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34063 | 100.01 | P11:25:EES:WATERF:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34063 | 100.01 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34063 | 100.01 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34063 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34063 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34063 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34063 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34063 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34063 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34063 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34063 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34063 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34063 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34063 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34164 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34165 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34178 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34178 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34189 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34189 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.3419 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34199 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34199 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34209 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34209 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.3422 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34254 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34254 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34341 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34383 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34425 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34469 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34486 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34497 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34512 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34513 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34517 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34518 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34634 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34707 | 107.18 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34712 | 106.47 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34712 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34716 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.3485 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34909 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34976 | 104.54 | Potential P4 Event - POI 527656_13 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.36396 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.63295 | 188.13 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.64289 | 187.42 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.64958 | 183.57 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.64958 | 183.59 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.64958 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.64958 | 195.61 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.65822 | 154.86 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31974 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.33393 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.63233 | 188.56 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.64224 | 187.81 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.64892 | 184.02 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.64892 | 184.11 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.64892 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.64892 | 196.06 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.65765 | 155.38 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2835 | 114.16 | GEN-2023-237_POI_560022_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35171 | 141.25 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35336 | 130.11 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35336 | 134.46 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35336 | 137.98 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35336 | 138.46 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35336 | 141.54 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35336 | 142.35 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35336 | 142.4 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35336 | 143.16 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35802 | 109.42 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35802 | 109.42 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3582 | 108.86 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3582 | 108.86 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35823 | 108.86 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35823 | 109.03 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35823 | 109.24 | P23:500:EES:PERRYVILLE:R7372::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.77 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.83 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.84 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.86 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.02 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.02 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.07 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.07 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.17 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.19 | P13:138:EES:LC:T1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.19 | P13:138:EES:LC:T2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.25 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.27 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.27 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.27 | P11:EHV:EES::1FRNTR 1!:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.29 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.31 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.31 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.36 | P13:230,22:CLEC::G2RODEMR::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.4 | P23:500:EES:PERRYVILLE:R3779::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.41 | P11:18:EES:NINEMI:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.51 | P13:230,22:CLEC::G3MADISN::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.52 | P11:HV:EES::1ISES U1:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.52 | P13:230:EES:NINEMI:AT4 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.53 | P11:EHV:EES::1ISES U2:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.54 | P11:22:CLEC:RODEMR1:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.54 | P11:26:EES:NINEMI:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.54 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.54 | P13:230:EES:NINEMI:AT5 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.55 | P11:26:EES:NINEMI:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.55 | P11:HV:EES::1NMIL U5!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.59 | P12:EHV:EES::8WHT BLUFF%:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.59 | P13:500:EES-EAI:WH_BLF:ST2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.6 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.6 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.62 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.66 | P13:345,24:CLEC::G1DOLHILL::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.73 | P12:EHV:EES::8ANO%:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.77 | P11:22:EES-EAI:ARK_NU:1:D395 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.85 | P11:21:EES:RVB:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.85 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.85 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.85 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.85 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.89 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.89 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.9 | P11:HV:EES::1LEWIS_U3 ST:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.95 | P11:25:EES:WATERF:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.95 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.95 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 110.17 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 110.17 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 110.17 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 110.25 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 110.25 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 110.3 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 111.11 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 111.53 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 111.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 114.16 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35825 | 109.36 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3583 | 108.84 | P13:345:OPPD:NEBCTY1G:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3583 | 108.84 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3583 | 108.84 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3583 | 109.07 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35831 | 109.19 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35832 | 109.14 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35832 | 109.14 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35833 | 109.27 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35833 | 109.27 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35834 | 108.67 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35842 | 109.33 | P23:345:WERE:WICH-345-50:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35843 | 109.35 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35844 | 109.5 | P13:69-138:AEPW:SHAM 2WT:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35844 | 109.62 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3585 | 109.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35859 | 109.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35861 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35865 | 109.36 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35865 | 109.75 | P23:345:WERE:BUFF-345-534:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35865 | 109.75 | P23:345:WERE:BUFF-345-543:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35895 | 110.42 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35896 | 111.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35906 | 111 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35906 | 111 | P23:345:SUNC:BU_BRK482:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35913 | 111.45 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35913 | 111.45 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35914 | 111.06 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35915 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35916 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35927 | 111.03 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35927 | 111.14 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35959 | 113.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35988 | 112.76 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35988 | 112.76 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36015 | 112.34 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36044 | 111.7 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36083 | 116.57 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36123 | 116 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36131 | 116.05 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36146 | 116.33 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36146 | 116.33 | Potential P4 Event - POI 531449_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36216 | 117.18 | POI 515800_22 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36216 | 117.33 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36345 | 121.98 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36345 | 122.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36347 | 119.68 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36925 | 118.53 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36925 | 120.63 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36925 | 120.63 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36946 | 124.63 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.59362 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30651 | 123.1 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30794 | 113.4 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30794 | 117.19 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30794 | 120.26 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30794 | 120.67 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30794 | 123.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30794 | 124.06 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30794 | 124.1 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30794 | 124.76 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31445 | 101.59 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3148 | 101.1 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31487 | 101.14 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.315 | 101.39 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.315 | 101.39 | Potential P4 Event - POI 531449_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31561 | 102.12 | POI 515800_22 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31561 | 102.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31674 | 106.31 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31674 | 107.11 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31675 | 104.3 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.32179 | 103.3 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.32179 | 105.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.32179 | 105.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.32197 | 108.62 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.57283 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.29261 | 188.65 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3002 | 139.38 | Potential P4 Event - POI 515458_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3013 | 139.3 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30172 | 137.63 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30216 | 133.93 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30233 | 138.51 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30274 | 163.83 | Potential P4 Event - POI 527656_0 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30288 | 136.02 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30326 | 163.21 | Potential P4 Event - POI 527656_13 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30326 | 163.21 | Potential P4 Event - POI 527656_14 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30347 | 161.82 | Potential P4 Event - POI 527656_9 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30362 | 161.31 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30362 | 161.31 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30362 | 164.87 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30362 | 164.87 | Potential P4 Event - POI 527656_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30387 | 138.87 | Potential P4 Event - POI 773600_4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30389 | 138.88 | Potential P4 Event - POI 773600_7 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30389 | 138.88 | Potential P4 Event - POI 773600_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30393 | 132.94 | P23:345:WERE:JEC-345-16:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30394 | 133 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30395 | 132.62 | 514796 IODINE-4 138 515376 WWRDEHV4 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30395 | 132.62 | 514796 IODINE-4 138 515533 REDCLFT4 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30395 | 133.01 | P23:345:WERE:JEC-345-20:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30397 | 132.82 | 532792 FR2EAST7 345 588364 G16-153-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30397 | 132.87 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30397 | 132.92 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30399 | 132.81 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30399 | 132.83 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30399 | 132.85 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30399 | 132.88 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30399 | 132.88 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.304 | 133.45 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.45 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.59 | 659387 KUMMERDG-BE3 345 659390 PATENTGT-BE3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.61 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.81 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.81 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.84 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.84 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.84 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.86 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.9 | P13:230,22:CLEC::G3MADISN::1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.9 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.91 | P12:069:GLHP:COLE-TURPIN-BEARD-ADAMS-JEFFERSON:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.93 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.94 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.95 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.96 | ASGI-2023-001_POI_528252_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.96 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.96 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.98 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.99 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.99 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.99 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.99 | P11:115:XEL:HBR #6 7 8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133 | P12:EHV:EES::8ISES%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133 | P23:345:XEL:8H14 PRI | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133 | P23:345:XEL:8H17 PRI AS | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.01 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.01 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.04 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.04 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.05 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.05 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.05 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.06 | P11:21:EES:RVB:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.06 | P11:HV:EES::1RVR_BND_G1!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.06 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.06 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.06 | P23:345:MEC:LOUISA 964 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.07 | P23:345:XEL:8N22 SHC | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.09 | P11:25:EES:WATERF:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.09 | P11:HV:EES::1WAT U3!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.09 | P13:230:EES:WATERF:T6:T7 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.09 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.09 | P23:345:MEC:CBEC 908 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.1 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.11 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.11 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.11 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.11 | P23:345:MEC:CBEC 905 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.15 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.18 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.19 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.19 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.21 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.28 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.3 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.47 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.76 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.88 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.24 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.42 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.43 | GEN-2023-201_POI_776000_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.91 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.91 | GEN-2023-236_POI_776700_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 138.67 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 138.67 | GEN-2023-081_POI_773600_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30402 | 132.96 | P23:500:EES-EAI:DELL:B8320::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30402 | 133.04 | P23:500:EES-EAI:INDEP2:B6126 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30418 | 133.26 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30419 | 133.29 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30428 | 133.57 | P42:345:OKGE:SB_SEOL7385:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3043 | 133.56 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30434 | 133.29 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30435 | 133.51 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30436 | 133.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30441 | 133.2 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30454 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30454 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30474 | 133.33 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30491 | 135.99 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30503 | 133.61 | P42:345:OKGE:SB_BAER7318:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30536 | 136.22 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30536 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30536 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30557 | 137.06 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3058 | 134.9 | P13:69-138:AEPW:SHAM 2WT:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3058 | 134.91 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3058 | 135.3 | P13:69-115:AEPW:SHAM 2WT:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3058 | 135.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30764 | 138.61 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30863 | 140.79 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30915 | 137.34 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.33465 | 163.65 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.33613 | 157.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.33613 | 157.17 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.33613 | 157.17 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.29261 | 190.26 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3002 | 141.48 | Potential P4 Event - POI 515458_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3013 | 142.25 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30172 | 138.3 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30216 | 135.66 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30233 | 140.57 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30274 | 167.97 | Potential P4 Event - POI 527656_0 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30288 | 137.76 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30326 | 167.9 | Potential P4 Event - POI 527656_13 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30326 | 167.9 | Potential P4 Event - POI 527656_14 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30327 | 166.55 | Potential P4 Event - POI 527656_10 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30357 | 134.6 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30362 | 165.89 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30362 | 165.89 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30362 | 169.93 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30362 | 169.93 | Potential P4 Event - POI 527656_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30387 | 142.83 | Potential P4 Event - POI 773600_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30389 | 142.91 | Potential P4 Event - POI 773600_7 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30389 | 142.91 | Potential P4 Event - POI 773600_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30393 | 134.9 | P23:345:WERE:JEC-345-16:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30394 | 134.92 | P13:345:OPPD:NEBCTY2G:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30395 | 134.63 | 514787 DEWEY 4 138 515533 REDCLFT4 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30395 | 134.93 | P23:345:WERE:JEC-345-20:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30395 | 134.94 | P11:345:WERE:JECU3-GEN:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30397 | 134.63 | 514789 MENOTAP4 138 514790 IMO 4 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30397 | 134.82 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30397 | 134.83 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30399 | 134.83 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30399 | 134.83 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30399 | 134.83 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.304 | 135.25 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.3 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.64 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.82 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.82 | P11:EHV:EES::1FRNTR 1!:1(1) | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.83 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.83 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.86 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.87 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.89 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.92 | P11:115:XEL:HBR #6 7 8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.92 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.92 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.93 | P13:345,24:CLEC::G1DOLHILL::1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.93 | P23:345:XEL:8H14 PRI | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.93 | P23:345:XEL:8H17 PRI AS | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.94 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.94 | P13:230,22:CLEC::G3MADISN::1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.95 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.96 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.96 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.96 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.96 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.97 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.97 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.97 | P23:345:XEL:8N22 SHC | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.97 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.98 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.98 | P23:345:MEC:LOUISA 964 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.99 | P23:345:MEC:CBEC 905 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.99 | P23:345:MEC:LOUISA 954 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.01 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.02 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.02 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.02 | P23:500:EES-EAI:WH_BLF:B7942 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.03 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.03 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.04 | P11:26:EES-EAI:INDEP2:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.04 | P11:26:EES-EAI:INDEP2:1:D401 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.04 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.04 | P11:EHV:EES::1ISES U2:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.04 | P11:HV:EES::1ISES U1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.05 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.05 | P12:EHV:EES::8ANO%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.05 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.06 | ASGI-2021-001_POI_766031_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.06 | ASGI-2023-001_POI_528252_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.06 | P11:22:EES-EAI:ARK_NU:1:D395 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.06 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.07 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.09 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.09 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.1 | P11:21:EES:RVB:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.11 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.11 | P11:EHV:EES::1ANO U2:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.14 | P11:25:EES:WATERF:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.14 | P11:HV:EES::1WAT U3!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.14 | P13:230:EES:WATERF:T6:T7 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.21 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.23 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.27 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.34 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 137.63 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 137.79 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 137.99 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 138.62 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 138.62 | GEN-2023-201_POI_776000_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 139.4 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 139.4 | GEN-2023-236_POI_776700_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 142.7 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 142.7 | GEN-2023-081_POI_773600_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3043 | 135.28 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30434 | 135.05 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30435 | 135.72 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30436 | 135.59 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30441 | 134.98 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30441 | 135.31 | P42:345:OKGE:SB_BVTY7387:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30454 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30454 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30474 | 135.19 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30491 | 138.08 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30503 | 135.54 | P42:345:OKGE:SB_BAER7318:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30536 | 137.62 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30536 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30536 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30557 | 139.08 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3058 | 136.85 | P13:69-138:AEPW:SHAM 2WT:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3058 | 136.86 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3058 | 137.23 | P13:69-115:AEPW:SHAM 2WT:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3058 | 137.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30764 | 140.18 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30863 | 142.88 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30915 | 139.06 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.33465 | 165.72 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.33613 | 159.05 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.33613 | 159.06 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.33613 | 159.06 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2022 | 188.13 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.202 | 188.56 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 162.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 164.73 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 164.73 | Potential P4 Event - POI 527656_11 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20168 | 165.04 | Potential P4 Event - POI 527656_13 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20168 | 165.04 | Potential P4 Event - POI 527656_14 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20192 | 165.64 | Potential P4 Event - POI 527656_0 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.202 | 164.89 | Potential P4 Event - POI 527656_10 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21015 | 109.73 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21015 | 110.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20042 | 124.23 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20447 | 138.42 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 128.24 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 131.95 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 135.41 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 135.88 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 138.79 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 139.6 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 139.63 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 140.37 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 119.52 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 119.53 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29756 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28714 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.01 | P11:25:EES:WATERF:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.01 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.01 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22324 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22435 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22435 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22435 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2245 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2245 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22456 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22456 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22469 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22474 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22595 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22628 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22629 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22646 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22651 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22685 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22685 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22783 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22816 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22825 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22841 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22847 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22848 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2301 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23078 | 107.18 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23083 | 106.47 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23083 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2319 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23285 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24205 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25113 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25198 | 104.54 | Potential P4 Event - POI 527656_13 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2663 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38265 | 154.86 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41996 | 188.13 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4214 | 187.42 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 183.57 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 183.59 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 195.61 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22208 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24432 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38232 | 155.38 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41955 | 188.56 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42097 | 187.81 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 184.02 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 184.11 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 196.06 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20042 | 124.63 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20447 | 141.25 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 130.11 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 134.46 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 137.98 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 138.46 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 141.54 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 142.35 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 142.4 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 143.16 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 118.53 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 120.63 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 120.63 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29756 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28714 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20097 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26012 | 154.86 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26048 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33028 | 187.42 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33256 | 188.13 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33273 | 183.57 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33273 | 183.59 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33273 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33273 | 195.61 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23899 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25989 | 155.38 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.32995 | 187.81 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.33223 | 188.56 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.33239 | 184.02 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.33239 | 184.11 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.33239 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.33239 | 196.06 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39619 | 139.3 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39677 | 139.38 | Potential P4 Event - POI 515458_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3973 | 133.93 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39739 | 137.63 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39783 | 136.02 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39797 | 138.87 | Potential P4 Event - POI 773600_4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39798 | 138.88 | Potential P4 Event - POI 773600_7 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39798 | 138.88 | Potential P4 Event - POI 773600_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.398 | 132.94 | P23:345:WERE:JEC-345-16:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.398 | 133 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39801 | 133.01 | P23:345:WERE:JEC-345-20:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39803 | 132.62 | 514796 IODINE-4 138 515376 WWRDEHV4 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39803 | 132.62 | 514796 IODINE-4 138 515533 REDCLFT4 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39803 | 132.82 | 532792 FR2EAST7 345 588364 G16-153-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39803 | 132.87 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39804 | 132.92 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39805 | 132.81 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39805 | 132.83 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39805 | 132.85 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39806 | 132.88 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39806 | 132.88 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39807 | 133.45 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.45 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.59 | 659387 KUMMERDG-BE3 345 659390 PATENTGT-BE3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.61 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.81 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.81 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.84 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.84 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.84 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.86 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.9 | P13:230,22:CLEC::G3MADISN::1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.9 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.91 | P12:069:GLHP:COLE-TURPIN-BEARD-ADAMS-JEFFERSON:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.93 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.94 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.95 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.96 | ASGI-2023-001_POI_528252_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.96 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.96 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.96 | P23:500:EES-EAI:DELL:B8320::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.98 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.99 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.99 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.99 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.99 | P11:115:XEL:HBR #6 7 8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133 | P12:EHV:EES::8ISES%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133 | P23:345:XEL:8H14 PRI | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133 | P23:345:XEL:8H17 PRI AS | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.01 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.01 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.04 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.04 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.04 | P23:500:EES-EAI:INDEP2:B6126 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.05 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.05 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.05 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.06 | P11:21:EES:RVB:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.06 | P11:HV:EES::1RVR_BND_G1!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.06 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.06 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.06 | P23:345:MEC:LOUISA 964 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.07 | P23:345:XEL:8N22 SHC | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.09 | P11:25:EES:WATERF:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.09 | P11:HV:EES::1WAT U3!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.09 | P13:230:EES:WATERF:T6:T7 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.09 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.09 | P23:345:MEC:CBEC 908 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.1 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.11 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.11 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.11 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.11 | P23:345:MEC:CBEC 905 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.15 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.18 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.19 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.19 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.21 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.28 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.3 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.47 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.76 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.88 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.24 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.42 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.43 | GEN-2023-201_POI_776000_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.91 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.91 | GEN-2023-236_POI_776700_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 138.67 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 138.67 | GEN-2023-081_POI_773600_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39818 | 133.26 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39822 | 133.29 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39831 | 133.51 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39832 | 133.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39845 | 133.29 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39848 | 133.33 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39848 | 133.56 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39852 | 133.2 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39853 | 133.57 | P42:345:OKGE:SB_SEOL7385:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39865 | 133.61 | P42:345:OKGE:SB_BAER7318:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39876 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39876 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3998 | 136.22 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3998 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3998 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39985 | 135.99 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39991 | 134.9 | P13:69-138:AEPW:SHAM 2WT:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39991 | 134.91 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39991 | 135.3 | P13:69-115:AEPW:SHAM 2WT:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39991 | 135.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4 | 188.65 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40095 | 137.34 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40154 | 138.51 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40397 | 138.61 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40422 | 137.06 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40556 | 140.79 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40881 | 163.83 | Potential P4 Event - POI 527656_0 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40891 | 161.82 | Potential P4 Event - POI 527656_9 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40897 | 163.21 | Potential P4 Event - POI 527656_13 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40897 | 163.21 | Potential P4 Event - POI 527656_14 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40906 | 161.31 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40906 | 161.31 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40906 | 164.87 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40906 | 164.87 | Potential P4 Event - POI 527656_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.43142 | 163.65 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4329 | 157.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4329 | 157.17 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4329 | 157.17 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39619 | 142.25 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39677 | 141.48 | Potential P4 Event - POI 515458_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3973 | 135.66 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39739 | 138.3 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39773 | 134.6 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39783 | 137.76 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39797 | 142.83 | Potential P4 Event - POI 773600_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39798 | 142.91 | Potential P4 Event - POI 773600_7 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39798 | 142.91 | Potential P4 Event - POI 773600_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.398 | 134.9 | P23:345:WERE:JEC-345-16:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.398 | 134.92 | P13:345:OPPD:NEBCTY2G:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39801 | 134.93 | P23:345:WERE:JEC-345-20:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39802 | 134.94 | P11:345:WERE:JECU3-GEN:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39803 | 134.63 | 514787 DEWEY 4 138 515533 REDCLFT4 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39803 | 134.83 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39804 | 134.63 | 514789 MENOTAP4 138 514790 IMO 4 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39804 | 134.82 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39805 | 134.83 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39806 | 134.83 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39806 | 134.83 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39807 | 135.25 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.3 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.64 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.82 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.82 | P11:EHV:EES::1FRNTR 1!:1(1) | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.83 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.83 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.86 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.87 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.89 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.92 | P11:115:XEL:HBR #6 7 8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.92 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.92 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.93 | P13:345,24:CLEC::G1DOLHILL::1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.93 | P23:345:XEL:8H14 PRI | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.93 | P23:345:XEL:8H17 PRI AS | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.94 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.94 | P13:230,22:CLEC::G3MADISN::1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.95 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.96 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.96 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.96 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.96 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.97 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.97 | P23:345:XEL:8N22 SHC | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.97 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.98 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.98 | P23:345:MEC:LOUISA 964 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.99 | P23:345:MEC:CBEC 905 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.99 | P23:345:MEC:LOUISA 954 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.01 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.02 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.02 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.02 | P23:500:EES-EAI:WH_BLF:B7942 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.03 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.03 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.04 | P11:26:EES-EAI:INDEP2:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.04 | P11:26:EES-EAI:INDEP2:1:D401 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.04 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.04 | P11:EHV:EES::1ISES U2:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.04 | P11:HV:EES::1ISES U1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.05 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.05 | P12:EHV:EES::8ANO%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.05 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.06 | ASGI-2021-001_POI_766031_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.06 | ASGI-2023-001_POI_528252_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.06 | P11:22:EES-EAI:ARK_NU:1:D395 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.06 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.07 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.09 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.09 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.1 | P11:21:EES:RVB:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.11 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.11 | P11:EHV:EES::1ANO U2:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.14 | P11:25:EES:WATERF:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.14 | P11:HV:EES::1WAT U3!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.14 | P13:230:EES:WATERF:T6:T7 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.21 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.23 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.27 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.34 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 137.63 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 137.79 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 137.99 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 138.62 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 138.62 | GEN-2023-201_POI_776000_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 139.4 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 139.4 | GEN-2023-236_POI_776700_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 142.7 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 142.7 | GEN-2023-081_POI_773600_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39809 | 134.97 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3983 | 135.31 | P42:345:OKGE:SB_BVTY7387:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39831 | 135.72 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39832 | 135.59 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39845 | 135.05 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39848 | 135.19 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39848 | 135.28 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39852 | 134.98 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39865 | 135.54 | P42:345:OKGE:SB_BAER7318:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39876 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39876 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3998 | 137.62 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3998 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3998 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39985 | 138.08 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39991 | 136.85 | P13:69-138:AEPW:SHAM 2WT:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39991 | 136.86 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39991 | 137.23 | P13:69-115:AEPW:SHAM 2WT:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39991 | 137.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4 | 190.26 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40095 | 139.06 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40154 | 140.57 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40397 | 140.18 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40422 | 139.08 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40556 | 142.88 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40881 | 167.97 | Potential P4 Event - POI 527656_0 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40897 | 167.9 | Potential P4 Event - POI 527656_13 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40897 | 167.9 | Potential P4 Event - POI 527656_14 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40906 | 165.89 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40906 | 165.89 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40906 | 169.93 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40906 | 169.93 | Potential P4 Event - POI 527656_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40908 | 166.55 | Potential P4 Event - POI 527656_10 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.43142 | 165.72 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4329 | 159.05 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4329 | 159.06 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4329 | 159.06 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21528 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20774 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.27109 | 154.86 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.29469 | 187.42 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.29671 | 183.57 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.29671 | 183.59 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.29671 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.29671 | 195.61 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.29784 | 188.13 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.27086 | 155.38 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2944 | 187.81 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2964 | 184.02 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2964 | 184.11 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2964 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2964 | 196.06 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.29755 | 188.56 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21528 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20774 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.20247 | 140.79 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21257 | 163.65 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21293 | 188.65 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21396 | 161.82 | Potential P4 Event - POI 527656_9 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21405 | 157.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21405 | 157.17 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21405 | 157.17 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21411 | 161.31 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21411 | 161.31 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21411 | 164.87 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21411 | 164.87 | Potential P4 Event - POI 527656_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21452 | 163.21 | Potential P4 Event - POI 527656_13 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21452 | 163.21 | Potential P4 Event - POI 527656_14 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21502 | 163.83 | Potential P4 Event - POI 527656_0 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.20247 | 142.88 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21257 | 165.72 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21293 | 190.26 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21405 | 159.05 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21405 | 159.06 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21405 | 159.06 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21411 | 165.89 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21411 | 165.89 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21411 | 169.93 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21411 | 169.93 | Potential P4 Event - POI 527656_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21452 | 167.9 | Potential P4 Event - POI 527656_13 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21452 | 167.9 | Potential P4 Event - POI 527656_14 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21474 | 166.55 | Potential P4 Event - POI 527656_10 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21502 | 167.97 | Potential P4 Event - POI 527656_0 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22039 | 109.05 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22039 | 109.05 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22058 | 108.48 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22058 | 108.48 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22061 | 108.48 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22061 | 108.65 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22061 | 108.87 | P23:500:EES:PERRYVILLE:R7372::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.39 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.46 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.48 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.64 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.64 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.67 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.67 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.79 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.82 | P13:138:EES:LC:T1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.82 | P13:138:EES:LC:T2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.87 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.89 | P11:EHV:EES::1FRNTR 1!:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.9 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.9 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.92 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.94 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.94 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.99 | P13:230,22:CLEC::G2RODEMR::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.99 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.03 | P23:500:EES:PERRYVILLE:R3779::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.04 | P11:18:EES:NINEMI:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.14 | P13:230,22:CLEC::G3MADISN::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.15 | P11:HV:EES::1ISES U1:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.15 | P13:230:EES:NINEMI:AT4 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.16 | P11:EHV:EES::1ISES U2:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.17 | P11:26:EES:NINEMI:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.17 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.17 | P13:230:EES:NINEMI:AT5 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.18 | P11:22:CLEC:RODEMR1:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.18 | P11:26:EES:NINEMI:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.18 | P11:HV:EES::1NMIL U5!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.22 | P12:EHV:EES::8WHT BLUFF%:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.22 | P13:500:EES-EAI:WH_BLF:ST2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.23 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.24 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.26 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.3 | P13:345,24:CLEC::G1DOLHILL::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.37 | P12:EHV:EES::8ANO%:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.4 | P11:22:EES-EAI:ARK_NU:1:D395 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.49 | P11:21:EES:RVB:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.49 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.49 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.49 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.49 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.53 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.53 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.53 | P11:HV:EES::1LEWIS_U3 ST:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.58 | P11:25:EES:WATERF:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.58 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.59 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.69 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.69 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.69 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.75 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.75 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.78 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 110.66 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 110.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 111.04 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 111.24 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 113.28 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22068 | 108.45 | P13:345:OPPD:NEBCTY1G:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22068 | 108.45 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22068 | 108.45 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22068 | 108.69 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22069 | 108.76 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2207 | 108.77 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22071 | 108.28 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22071 | 108.82 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22071 | 108.9 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22071 | 108.9 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22083 | 108.95 | P23:345:WERE:WICH-345-50:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22083 | 108.98 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22089 | 108.99 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.221 | 109.44 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22105 | 109.13 | P13:69-138:AEPW:SHAM 2WT:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22105 | 109.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22107 | 108.99 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22109 | 109.39 | P23:345:WERE:BUFF-345-534:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22109 | 109.39 | P23:345:WERE:BUFF-345-543:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22163 | 111.09 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22163 | 111.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22163 | 111.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22173 | 110.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22173 | 110.68 | P23:345:SUNC:BU_BRK482:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22176 | 110.1 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22178 | 110.71 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22178 | 110.82 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22191 | 110.77 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22254 | 111.03 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22254 | 111.04 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22267 | 112.1 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22302 | 111.42 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2243 | 115.8 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22436 | 115.86 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22452 | 116.15 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22452 | 116.15 | Potential P4 Event - POI 531449_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22513 | 113.28 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22542 | 112.35 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22542 | 112.35 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22572 | 116.25 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22614 | 117.38 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22698 | 117.14 | POI 515800_22 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22698 | 117.29 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23029 | 124.23 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23079 | 138.42 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23115 | 121.61 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23115 | 122.52 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23186 | 128.24 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23186 | 131.95 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23186 | 135.41 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23186 | 135.88 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23186 | 138.79 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23186 | 139.6 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23186 | 139.63 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23186 | 140.37 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23638 | 119.52 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23638 | 119.53 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.24072 | 118.97 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36557 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20069 | 108.27 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20112 | 120.63 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20144 | 105.99 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20144 | 106.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20206 | 111.76 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20206 | 115 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20206 | 118.01 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20206 | 118.42 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20206 | 120.96 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20206 | 121.66 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20206 | 121.68 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20206 | 122.33 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.206 | 104.17 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.206 | 104.17 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20978 | 103.69 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.35277 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23605 | 100.01 | P11:25:EES:WATERF:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23605 | 100.01 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23605 | 100.01 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23605 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23605 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23605 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23605 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23605 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23605 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23605 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23605 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23605 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23605 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23605 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23724 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23747 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23748 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23748 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23762 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23762 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23769 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23769 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23772 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23787 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23855 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23892 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23893 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23905 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23955 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24126 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24132 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24135 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24151 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24156 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24157 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24167 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24167 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24319 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24385 | 107.18 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24391 | 106.47 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24391 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24532 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24817 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2486 | 104.54 | Potential P4 Event - POI 527656_13 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25197 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25331 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25619 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.43191 | 154.86 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.44359 | 188.13 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.44612 | 187.42 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.45016 | 183.57 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.45016 | 183.59 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.45016 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.45016 | 195.61 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23118 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23505 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.43153 | 155.38 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.44315 | 188.56 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.44566 | 187.81 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4497 | 184.02 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4497 | 184.11 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4497 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4497 | 196.06 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22039 | 109.42 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22039 | 109.42 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22058 | 108.86 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22058 | 108.86 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22061 | 108.86 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22061 | 109.03 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22061 | 109.24 | P23:500:EES:PERRYVILLE:R7372::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.77 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.83 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.84 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.86 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.02 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.02 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.07 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.07 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.17 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.19 | P13:138:EES:LC:T1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.19 | P13:138:EES:LC:T2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.25 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.27 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.27 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.27 | P11:EHV:EES::1FRNTR 1!:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.29 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.31 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.31 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.36 | P13:230,22:CLEC::G2RODEMR::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.36 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.4 | P23:500:EES:PERRYVILLE:R3779::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.41 | P11:18:EES:NINEMI:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.51 | P13:230,22:CLEC::G3MADISN::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.52 | P11:HV:EES::1ISES U1:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.52 | P13:230:EES:NINEMI:AT4 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.53 | P11:EHV:EES::1ISES U2:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.54 | P11:22:CLEC:RODEMR1:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.54 | P11:26:EES:NINEMI:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.54 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.54 | P13:230:EES:NINEMI:AT5 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.55 | P11:26:EES:NINEMI:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.55 | P11:HV:EES::1NMIL U5!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.59 | P12:EHV:EES::8WHT BLUFF%:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.59 | P13:500:EES-EAI:WH_BLF:ST2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.6 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.6 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.62 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.66 | P13:345,24:CLEC::G1DOLHILL::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.73 | P12:EHV:EES::8ANO%:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.77 | P11:22:EES-EAI:ARK_NU:1:D395 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.85 | P11:21:EES:RVB:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.85 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.85 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.85 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.85 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.89 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.89 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.9 | P11:HV:EES::1LEWIS_U3 ST:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.95 | P11:25:EES:WATERF:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.95 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.95 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 110.17 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 110.17 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 110.17 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 110.25 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 110.25 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 110.3 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 111.11 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 111.53 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 111.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 114.16 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22068 | 108.84 | P13:345:OPPD:NEBCTY1G:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22068 | 108.84 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22068 | 108.84 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22068 | 109.07 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22069 | 109.14 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2207 | 109.14 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22071 | 108.67 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22071 | 109.19 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22071 | 109.27 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22071 | 109.27 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22083 | 109.33 | P23:345:WERE:WICH-345-50:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22083 | 109.35 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22089 | 109.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.221 | 109.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22105 | 109.5 | P13:69-138:AEPW:SHAM 2WT:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22105 | 109.62 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22107 | 109.36 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22109 | 109.75 | P23:345:WERE:BUFF-345-534:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22109 | 109.75 | P23:345:WERE:BUFF-345-543:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22163 | 111.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22163 | 111.45 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22163 | 111.45 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22173 | 111 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22173 | 111 | P23:345:SUNC:BU_BRK482:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22176 | 110.42 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22178 | 111.03 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22178 | 111.14 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22191 | 111.06 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22254 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22254 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22267 | 112.34 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22278 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22302 | 111.7 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2243 | 116 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22436 | 116.05 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22452 | 116.33 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22452 | 116.33 | Potential P4 Event - POI 531449_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22513 | 113.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22542 | 112.76 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22542 | 112.76 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22572 | 116.57 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22698 | 117.18 | POI 515800_22 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22698 | 117.33 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23029 | 124.63 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23079 | 141.25 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23115 | 121.98 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23115 | 122.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23186 | 130.11 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23186 | 134.46 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23186 | 137.98 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23186 | 138.46 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23186 | 141.54 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23186 | 142.35 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23186 | 142.4 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23186 | 143.16 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23638 | 118.53 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23638 | 120.63 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23638 | 120.63 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.24072 | 119.68 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36557 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20069 | 108.62 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20112 | 123.1 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20144 | 106.31 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20144 | 107.11 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20206 | 113.4 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20206 | 117.19 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20206 | 120.26 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20206 | 120.67 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20206 | 123.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20206 | 124.06 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20206 | 124.1 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20206 | 124.76 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.206 | 103.3 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.206 | 105.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.206 | 105.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20978 | 104.3 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.35277 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.3973 | 106.36 | P12:115:SPS:T49_1_PRNGLE_BLKHK:::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.3973 | 110.41 | 523214 WRB_REF 115 523346 BLKHAWK_E 3 115 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.40131 | 107.79 | 523551 HUTCHISON 6 230 524044 NICHOLS 6 230 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41541 | 105.4 | P12:230:SPS:K98::1_CHANN_XIT:: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41546 | 103.32 | P12:345:OKGE:BKRBKR604_2 :::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41551 | 102.8 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41551 | 102.99 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41552 | 102.39 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41552 | 102.4 | 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41552 | 102.64 | 539117 SPRVILL-EHVB 230 539695 SPEARVL6 230 Z1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41552 | 102.68 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41552 | 102.84 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41552 | 102.84 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41552 | 102.85 | P11:24:NPPD:GENTLM2G:2:757:: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41553 | 102.7 | P11:230:WERE:JECU1-GEN:::HV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41553 | 102.7 | P11:345:WERE:JECU3-GEN:::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41553 | 102.71 | P23:345:WERE:JEC-345-20:::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.24 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.37 | P12:EHV:EES::8PERRYVILLE%:1(1) | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.37 | P12:HV:EES::6LEWISCREEK!:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.39 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.39 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.39 | P11:EHV:EES::1FRNTR 1!:1(1) | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.39 | P11:HV:EES::1CARVLE_C1!:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.39 | P12:LV-EHV:EES::7GRIMES%:1FRNTR 1!:1FRNTR 2!:1FRNTR 3!:1FRNTR 4!:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.4 | 659387 KUMMERDG-BE3 345 659390 PATENTGT-BE3 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.4 | P12:LV-HV:EES::6GYPSY%:1GYP U3!:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.61 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.63 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.63 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.63 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.64 | P11:18:HAST::EGYCTR2G WEC2:LOSS OF WEC 2 GEN:HV:: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.64 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU:HV:: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.64 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.65 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.65 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.66 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.69 | P23:345:MEC:LOUISA 964 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.7 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.7 | P23:345:XEL:8H14 PRI | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.71 | P11:115:XEL:HBR #6 7 8 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.71 | P23:345:XEL:8H17 PRI AS | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.74 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.74 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.74 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.75 | P23:345:XEL:8N17 SHC | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.75 | P23:345:XEL:8N22 SHC | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.76 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.76 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.76 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.76 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.78 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.78 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.79 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.79 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.79 | P23:345:MEC:CBEC 908 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.8 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.81 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.82 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.82 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.82 | P23:345:MEC:CBEC 905 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.83 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.84 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.85 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.85 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.85 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.86 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.93 | 772281 GEN-2023-015 345 772282 G23-015XFMR1 34.5 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.05 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.1 | 772181 GEN-2023-010 230 772182 G23-010XFMR1 34.5 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.1 | 772181 GEN-2023-010 230 772185 G23-010XFMR2 34.5 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.27 | P12:115:GLHP:POWELL-LOBO-DRYTRAILS:::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.59 | ASGI-2011-002_POI_523266_Generator_outage | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.69 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.69 | ASGI-2016-010_POI_523090_Generator_outage | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.8 | GEN-2023-010_POI_523309_Generator_outage | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.83 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.83 | GEN-2017-100_POI_523090_Generator_outage | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.07 | GEN-2002-009_POI_523195_Generator_outage | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.28 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.28 | GEN-2017-047_POI_523120_Generator_outage | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 108.72 | 523344 BLKHAWK_W 3 115 523461 BLACKHAWK1 1 13.8 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 109.32 | 523346 BLKHAWK_E 3 115 523462 BLACKHAWK2 1 13.8 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 102.61 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 102.63 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 102.64 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 102.67 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 102.68 | P23:500:EAI-TVA:NBF_WEST M~1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 102.68 | P23:500:EES-EAI:KEO:B4931 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 102.74 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 102.83 | P23:500:EES-EAI:KEO:B4921 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 102.85 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 102.86 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41556 | 102.65 | P12:345:WERE:VIOL-WICH-345:::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41556 | 102.71 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41556 | 102.75 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41558 | 102.91 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41558 | 102.93 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41558 | 102.94 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.4156 | 102.72 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.4156 | 102.96 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.4156 | 102.96 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.4156 | 104.22 | Potential P4 Event - POI 527656_13 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.4156 | 104.22 | Potential P4 Event - POI 527656_14 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41561 | 102.91 | P23:345:AEPW:PITTSBURG CB 3445A NBTB:::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41561 | 102.91 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT:::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41565 | 102.97 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41565 | 102.99 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41567 | 102.96 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41568 | 103.13 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41568 | 103.76 | Potential P4 Event - POI 560022_9 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41568 | 103.76 | Potential P4 Event - POI 762216_5 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41572 | 103.27 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41574 | 103.31 | Potential P4 Event - POI 515800_13 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41575 | 104.01 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41575 | 104.06 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41575 | 104.06 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.4158 | 103.33 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41601 | 104.74 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41604 | 104.45 | 515375 WWRDEHV7 345 516059 BECKHAM7 345 2 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41604 | 104.45 | P12:345:OKGE:BKRBKR489:::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41612 | 108.13 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41612 | 108.88 | Potential P4 Event - POI 523097_19 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41618 | 104.6 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41618 | 104.97 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41704 | 102.96 | 523977 HARRNG_WST 6 230 523978 HARRNG_MID 6 230 @1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41739 | 118.02 | Potential P4 Event - POI 523097_33 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41739 | 118.02 | Potential P4 Event - POI 523961_4 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41768 | 106.28 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41775 | 105.51 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41775 | 105.52 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.43138 | 119.63 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.44784 | 107.5 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 1 | 144.49 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.3973 | 107.91 | P12:115:SPS:T49_1_PRNGLE_BLKHK:::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.3973 | 112.56 | 523214 WRB_REF 115 523346 BLKHAWK_E 3 115 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.40131 | 109.48 | 523551 HUTCHISON 6 230 524044 NICHOLS 6 230 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41541 | 107.1 | P12:230:SPS:K98::1_CHANN_XIT:: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41546 | 104.95 | P12:345:OKGE:BKRBKR604_2 :::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41551 | 104.41 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41551 | 104.63 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41552 | 103.97 | 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41552 | 104.25 | 539117 SPRVILL-EHVB 230 539695 SPEARVL6 230 Z1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41552 | 104.28 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41552 | 104.47 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41552 | 104.47 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41552 | 104.49 | P11:24:NPPD:GENTLM2G:2:757:: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41553 | 103.99 | 640183 GENTLMN3 345 640500 THEDFRD3 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41553 | 104.2 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41553 | 104.31 | P11:230:WERE:JECU1-GEN:::HV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41553 | 104.31 | P11:345:WERE:JECU3-GEN:::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41553 | 104.32 | P23:345:WERE:JEC-345-20:::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.8 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.96 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.96 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.96 | P11:EHV:EES::1FRNTR 1!:1(1) | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.97 | 659387 KUMMERDG-BE3 345 659390 PATENTGT-BE3 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.98 | P12:LV-HV:EES::6GYPSY%:1GYP U3!:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.99 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.99 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.99 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.99 | P11:HV:EES::FLINTCR1:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.99 | P12:HV:EES::4LEWIS%:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.99 | P12:LV-HV:EES::3GYPSY%:1GYP U2!:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.2 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.21 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.23 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.23 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.23 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.24 | P11:18:HAST::EGYCTR2G WEC2:LOSS OF WEC 2 GEN:HV:: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.24 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU:HV:: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.24 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.25 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.25 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.27 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.3 | P23:345:MEC:LOUISA 964 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.31 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.32 | P11:115:XEL:HBR #6 7 8 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.32 | P23:345:XEL:8H14 PRI | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.32 | P23:345:XEL:8H17 PRI AS | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.35 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.35 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.36 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.37 | P23:345:XEL:8N17 SHC | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.37 | P23:345:XEL:8N22 SHC | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.38 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.38 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.39 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.39 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.4 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.41 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.41 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.41 | P23:345:MEC:CBEC 908 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.42 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.43 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.44 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.45 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.45 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.45 | P23:345:MEC:CBEC 905 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.47 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.48 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.48 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.49 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.49 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.5 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.55 | 772281 GEN-2023-015 345 772282 G23-015XFMR1 34.5 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.7 | 772181 GEN-2023-010 230 772182 G23-010XFMR1 34.5 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.7 | 772181 GEN-2023-010 230 772185 G23-010XFMR2 34.5 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.71 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.87 | P12:115:GLHP:POWELL-LOBO-DRYTRAILS:::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 105.21 | ASGI-2011-002_POI_523266_Generator_outage | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 105.3 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 105.3 | ASGI-2016-010_POI_523090_Generator_outage | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 105.37 | GEN-2023-010_POI_523309_Generator_outage | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 105.43 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 105.43 | GEN-2017-100_POI_523090_Generator_outage | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 105.71 | GEN-2002-009_POI_523195_Generator_outage | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 105.88 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 105.88 | GEN-2017-047_POI_523120_Generator_outage | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 110.18 | 523344 BLKHAWK_W 3 115 523461 BLACKHAWK1 1 13.8 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 110.76 | 523346 BLKHAWK_E 3 115 523462 BLACKHAWK2 1 13.8 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 104.21 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 104.23 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 104.24 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 104.27 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 104.28 | P23:500:EAI-TVA:NBF_WEST M~1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 104.28 | P23:500:EES-EAI:KEO:B4931 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 104.35 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 104.45 | P23:500:EES-EAI:KEO:B4921 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 104.48 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 104.49 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41556 | 104.25 | P12:345:WERE:VIOL-WICH-345:::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41556 | 104.32 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41556 | 104.36 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41557 | 104.2 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41558 | 104.53 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41558 | 104.55 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41558 | 104.59 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41558 | 104.6 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.4156 | 104.33 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.4156 | 104.6 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.4156 | 104.6 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.4156 | 105.82 | Potential P4 Event - POI 527656_13 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.4156 | 105.82 | Potential P4 Event - POI 527656_14 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41561 | 104.54 | P23:345:AEPW:PITTSBURG CB 3445A NBTB:::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41561 | 104.54 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT:::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41565 | 104.6 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41565 | 104.62 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41568 | 104.8 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41568 | 105.44 | Potential P4 Event - POI 560022_9 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41568 | 105.44 | Potential P4 Event - POI 762216_5 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41572 | 104.93 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41575 | 105.74 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41575 | 105.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41575 | 105.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.4158 | 105.04 | POI 515800_22 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.4158 | 105.08 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41601 | 106.47 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41604 | 106.17 | 515375 WWRDEHV7 345 516059 BECKHAM7 345 2 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41604 | 106.17 | P12:345:OKGE:BKRBKR489:::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41612 | 110 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41618 | 106.42 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41618 | 106.88 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41704 | 104.63 | 523977 HARRNG_WST 6 230 523978 HARRNG_MID 6 230 @1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41717 | 110.9 | Potential P4 Event - POI 515375_50 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41739 | 120.48 | Potential P4 Event - POI 523097_33 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41739 | 120.48 | Potential P4 Event - POI 523961_4 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41768 | 108.17 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41775 | 107.33 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41775 | 107.34 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.43138 | 122.18 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.44784 | 109.15 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 1 | 144.35 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.344 | 188.65 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.34874 | 139.38 | Potential P4 Event - POI 515458_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.34955 | 139.3 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35016 | 137.63 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3504 | 133.93 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35109 | 136.02 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3519 | 138.87 | Potential P4 Event - POI 773600_4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35192 | 138.88 | Potential P4 Event - POI 773600_7 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35192 | 138.88 | Potential P4 Event - POI 773600_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35195 | 132.94 | P23:345:WERE:JEC-345-16:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35195 | 133 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35197 | 132.62 | 514796 IODINE-4 138 515376 WWRDEHV4 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35197 | 132.62 | 514796 IODINE-4 138 515533 REDCLFT4 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35197 | 133.01 | P23:345:WERE:JEC-345-20:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35198 | 132.87 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35199 | 132.82 | 532792 FR2EAST7 345 588364 G16-153-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35199 | 132.92 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.352 | 132.81 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.352 | 132.83 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35201 | 132.85 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35201 | 132.88 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35201 | 132.88 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35202 | 133.45 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.45 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.59 | 659387 KUMMERDG-BE3 345 659390 PATENTGT-BE3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.61 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.81 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.81 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.84 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.84 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.84 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.86 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.9 | P13:230,22:CLEC::G3MADISN::1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.9 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.93 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.94 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.95 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.96 | ASGI-2023-001_POI_528252_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.96 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.96 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.96 | P23:500:EES-EAI:DELL:B8320::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.98 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.99 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.99 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.99 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.99 | P11:115:XEL:HBR #6 7 8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133 | P12:EHV:EES::8ISES%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133 | P23:345:XEL:8H14 PRI | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133 | P23:345:XEL:8H17 PRI AS | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.01 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.01 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.04 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.04 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.05 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.05 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.05 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.06 | P11:21:EES:RVB:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.06 | P11:HV:EES::1RVR_BND_G1!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.06 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.06 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.06 | P23:345:MEC:LOUISA 964 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.07 | P23:345:XEL:8N22 SHC | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.09 | P11:25:EES:WATERF:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.09 | P11:HV:EES::1WAT U3!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.09 | P13:230:EES:WATERF:T6:T7 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.09 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.09 | P23:345:MEC:CBEC 908 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.1 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.11 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.11 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.11 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.11 | P23:345:MEC:CBEC 905 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.15 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.18 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.19 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.19 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.21 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.28 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.3 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.47 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.76 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.88 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.24 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.42 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.43 | GEN-2023-201_POI_776000_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.91 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.91 | GEN-2023-236_POI_776700_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 138.67 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 138.67 | GEN-2023-081_POI_773600_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35204 | 133.04 | P23:500:EES-EAI:INDEP2:B6126 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35206 | 132.91 | P12:069:GLHP:COLE-TURPIN-BEARD-ADAMS-JEFFERSON:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35216 | 133.26 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35219 | 133.29 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35232 | 133.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35232 | 133.51 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35235 | 133.56 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35236 | 133.57 | P42:345:OKGE:SB_SEOL7385:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35238 | 133.29 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35244 | 133.2 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3526 | 133.33 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35261 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35261 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35283 | 133.61 | P42:345:OKGE:SB_BAER7318:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35313 | 135.99 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35349 | 136.22 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35349 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35349 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35369 | 163.83 | Potential P4 Event - POI 527656_0 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35412 | 163.21 | Potential P4 Event - POI 527656_13 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35412 | 163.21 | Potential P4 Event - POI 527656_14 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35425 | 161.82 | Potential P4 Event - POI 527656_9 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35437 | 134.9 | P13:69-138:AEPW:SHAM 2WT:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35437 | 134.91 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35437 | 135.3 | P13:69-115:AEPW:SHAM 2WT:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35437 | 135.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35441 | 161.31 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35441 | 161.31 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35441 | 164.87 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35441 | 164.87 | Potential P4 Event - POI 527656_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35606 | 137.34 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35631 | 138.61 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35746 | 140.79 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.38567 | 137.06 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39848 | 163.65 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39996 | 157.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39996 | 157.17 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39996 | 157.17 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.42762 | 138.51 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.344 | 190.26 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.34874 | 141.48 | Potential P4 Event - POI 515458_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.34955 | 142.25 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35016 | 138.3 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3504 | 135.66 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35109 | 137.76 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35163 | 134.6 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3519 | 142.83 | Potential P4 Event - POI 773600_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35192 | 142.91 | Potential P4 Event - POI 773600_7 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35192 | 142.91 | Potential P4 Event - POI 773600_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35195 | 134.9 | P23:345:WERE:JEC-345-16:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35195 | 134.92 | P13:345:OPPD:NEBCTY2G:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35197 | 134.63 | 514787 DEWEY 4 138 515533 REDCLFT4 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35197 | 134.93 | P23:345:WERE:JEC-345-20:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35197 | 134.94 | P11:345:WERE:JECU3-GEN:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35198 | 134.83 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35199 | 134.63 | 514789 MENOTAP4 138 514790 IMO 4 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35199 | 134.82 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35201 | 134.83 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35201 | 134.83 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35201 | 134.83 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35202 | 135.25 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.3 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.64 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.82 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.82 | P11:EHV:EES::1FRNTR 1!:1(1) | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.83 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.83 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.86 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.87 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.89 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.92 | P11:115:XEL:HBR #6 7 8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.92 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.92 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.93 | P13:345,24:CLEC::G1DOLHILL::1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.93 | P23:345:XEL:8H14 PRI | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.93 | P23:345:XEL:8H17 PRI AS | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.94 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.94 | P13:230,22:CLEC::G3MADISN::1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.95 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.96 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.96 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.96 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.96 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.97 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.97 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.97 | P23:345:XEL:8N22 SHC | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.97 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.98 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.98 | P23:345:MEC:LOUISA 964 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.99 | P23:345:MEC:CBEC 905 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.99 | P23:345:MEC:LOUISA 954 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.01 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.02 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.02 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.02 | P23:500:EES-EAI:WH_BLF:B7942 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.03 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.03 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.04 | P11:26:EES-EAI:INDEP2:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.04 | P11:26:EES-EAI:INDEP2:1:D401 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.04 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.04 | P11:EHV:EES::1ISES U2:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.04 | P11:HV:EES::1ISES U1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.05 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.05 | P12:EHV:EES::8ANO%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.05 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.06 | ASGI-2021-001_POI_766031_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.06 | ASGI-2023-001_POI_528252_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.06 | P11:22:EES-EAI:ARK_NU:1:D395 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.06 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.07 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.09 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.09 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.1 | P11:21:EES:RVB:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.11 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.11 | P11:EHV:EES::1ANO U2:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.14 | P11:25:EES:WATERF:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.14 | P11:HV:EES::1WAT U3!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.14 | P13:230:EES:WATERF:T6:T7 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.21 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.23 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.27 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.34 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 137.63 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 137.79 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 137.99 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 138.62 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 138.62 | GEN-2023-201_POI_776000_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 139.4 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 139.4 | GEN-2023-236_POI_776700_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 142.7 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 142.7 | GEN-2023-081_POI_773600_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35232 | 135.59 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35232 | 135.72 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35234 | 135.31 | P42:345:OKGE:SB_BVTY7387:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35235 | 135.28 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35238 | 135.05 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35244 | 134.98 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3526 | 135.19 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35261 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35261 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35283 | 135.54 | P42:345:OKGE:SB_BAER7318:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35313 | 138.08 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35349 | 137.62 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35349 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35349 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35369 | 167.97 | Potential P4 Event - POI 527656_0 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35412 | 167.9 | Potential P4 Event - POI 527656_13 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35412 | 167.9 | Potential P4 Event - POI 527656_14 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35415 | 166.55 | Potential P4 Event - POI 527656_10 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35437 | 136.85 | P13:69-138:AEPW:SHAM 2WT:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35437 | 136.86 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35437 | 137.23 | P13:69-115:AEPW:SHAM 2WT:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35437 | 137.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35441 | 165.89 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35441 | 165.89 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35441 | 169.93 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35441 | 169.93 | Potential P4 Event - POI 527656_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35606 | 139.06 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35631 | 140.18 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35746 | 142.88 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.38567 | 139.08 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39848 | 165.72 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39996 | 159.05 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39996 | 159.06 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39996 | 159.06 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.42762 | 140.57 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20193 | 154.86 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22394 | 187.42 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22507 | 183.57 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22507 | 183.59 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22507 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22507 | 195.61 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22911 | 188.13 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.20176 | 155.38 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22371 | 187.81 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22484 | 184.02 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22484 | 184.11 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22484 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22484 | 196.06 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22888 | 188.56 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 162.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 164.73 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 164.73 | Potential P4 Event - POI 527656_11 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20168 | 165.04 | Potential P4 Event - POI 527656_13 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20168 | 165.04 | Potential P4 Event - POI 527656_14 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20192 | 165.64 | Potential P4 Event - POI 527656_0 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.202 | 164.89 | Potential P4 Event - POI 527656_10 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21015 | 109.73 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21015 | 110.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20042 | 124.23 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20447 | 138.42 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 128.24 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 131.95 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 135.41 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 135.88 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 138.79 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 139.6 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 139.63 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 140.37 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 119.52 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 119.53 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29756 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28714 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.01 | P11:25:EES:WATERF:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.01 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.01 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22324 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22435 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22435 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22435 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2245 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2245 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22456 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22456 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22469 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22474 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22595 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22628 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22629 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22646 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22651 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22685 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22685 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22783 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22816 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22825 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22841 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22847 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22848 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2301 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23078 | 107.18 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23083 | 106.47 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23083 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2319 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23285 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24205 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25113 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25198 | 104.54 | Potential P4 Event - POI 527656_13 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2663 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38265 | 154.86 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41996 | 188.13 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4214 | 187.42 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 183.57 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 183.59 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 195.61 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22208 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24432 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38232 | 155.38 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41955 | 188.56 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42097 | 187.81 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 184.02 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 184.11 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 196.06 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20042 | 124.63 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20447 | 141.25 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 130.11 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 134.46 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 137.98 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 138.46 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 141.54 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 142.35 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 142.4 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 143.16 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 118.53 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 120.63 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 120.63 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29756 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28714 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 162.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 164.73 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 164.73 | Potential P4 Event - POI 527656_11 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20168 | 165.04 | Potential P4 Event - POI 527656_13 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20168 | 165.04 | Potential P4 Event - POI 527656_14 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20192 | 165.64 | Potential P4 Event - POI 527656_0 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.202 | 164.89 | Potential P4 Event - POI 527656_10 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21015 | 109.73 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21015 | 110.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20042 | 124.23 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20447 | 138.42 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 128.24 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 131.95 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 135.41 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 135.88 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 138.79 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 139.6 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 139.63 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 140.37 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 119.52 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 119.53 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29756 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28714 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.01 | P11:25:EES:WATERF:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.01 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.01 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22324 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22435 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22435 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22435 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2245 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2245 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22456 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22456 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22469 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22474 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22595 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22628 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22629 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22646 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22651 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22685 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22685 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22783 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22816 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22825 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22841 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22847 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22848 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2301 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23078 | 107.18 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23083 | 106.47 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23083 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2319 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23285 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24205 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25113 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25198 | 104.54 | Potential P4 Event - POI 527656_13 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2663 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38265 | 154.86 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41996 | 188.13 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4214 | 187.42 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 183.57 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 183.59 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 195.61 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22208 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24432 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38232 | 155.38 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41955 | 188.56 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42097 | 187.81 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 184.02 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 184.11 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 196.06 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20042 | 124.63 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20447 | 141.25 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 130.11 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 134.46 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 137.98 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 138.46 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 141.54 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 142.35 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 142.4 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 143.16 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 118.53 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 120.63 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 120.63 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29756 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28714 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22137 | 162.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22137 | 164.73 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22137 | 164.73 | Potential P4 Event - POI 527656_11 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22137 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22153 | 165.04 | Potential P4 Event - POI 527656_13 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22153 | 165.04 | Potential P4 Event - POI 527656_14 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22183 | 165.64 | Potential P4 Event - POI 527656_0 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.2219 | 164.89 | Potential P4 Event - POI 527656_10 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.22144 | 109.73 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.22144 | 110.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20067 | 138.42 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 128.24 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 131.95 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 135.41 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 135.88 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 138.79 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 139.6 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 139.63 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 140.37 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20774 | 119.52 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20774 | 119.53 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.28014 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.27032 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.01 | P11:25:EES:WATERF:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.01 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.01 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22642 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22643 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22643 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22657 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22657 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22664 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22664 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22678 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22681 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22771 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22803 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22804 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22838 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22838 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22842 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22843 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22855 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23021 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2303 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23046 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23052 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23052 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23068 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23137 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.232 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23281 | 107.18 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23286 | 106.47 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23286 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23492 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24452 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25473 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25581 | 104.54 | Potential P4 Event - POI 527656_13 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.27549 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37554 | 154.86 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42379 | 188.13 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42533 | 187.42 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42908 | 183.57 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42908 | 183.59 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42908 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42908 | 195.61 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22435 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25276 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37521 | 155.38 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42338 | 188.56 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4249 | 187.81 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42864 | 184.02 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42864 | 184.11 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42864 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42864 | 196.06 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20067 | 141.25 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 130.11 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 134.46 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 137.98 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 138.46 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 141.54 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 142.35 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 142.4 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 143.16 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20774 | 118.53 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20774 | 120.63 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20774 | 120.63 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.28014 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.27032 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22137 | 162.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22137 | 164.73 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22137 | 164.73 | Potential P4 Event - POI 527656_11 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22137 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22153 | 165.04 | Potential P4 Event - POI 527656_13 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22153 | 165.04 | Potential P4 Event - POI 527656_14 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22183 | 165.64 | Potential P4 Event - POI 527656_0 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.2219 | 164.89 | Potential P4 Event - POI 527656_10 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.22144 | 109.73 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.22144 | 110.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20067 | 138.42 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 128.24 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 131.95 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 135.41 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 135.88 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 138.79 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 139.6 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 139.63 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 140.37 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20774 | 119.52 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20774 | 119.53 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.28014 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.27032 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.01 | P11:25:EES:WATERF:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.01 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.01 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22642 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22643 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22643 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22657 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22657 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22664 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22664 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22678 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22681 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22771 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22803 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22804 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22838 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22838 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22842 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22843 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22855 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23021 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2303 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23046 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23052 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23052 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23068 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23137 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.232 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23281 | 107.18 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23286 | 106.47 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23286 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23492 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24452 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25473 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25581 | 104.54 | Potential P4 Event - POI 527656_13 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.27549 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37554 | 154.86 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42379 | 188.13 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42533 | 187.42 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42908 | 183.57 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42908 | 183.59 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42908 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42908 | 195.61 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22435 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25276 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37521 | 155.38 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42338 | 188.56 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4249 | 187.81 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42864 | 184.02 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42864 | 184.11 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42864 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42864 | 196.06 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20067 | 141.25 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 130.11 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 134.46 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 137.98 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 138.46 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 141.54 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 142.35 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 142.4 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 143.16 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20774 | 118.53 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20774 | 120.63 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20774 | 120.63 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.28014 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.27032 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 162.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 164.73 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 164.73 | Potential P4 Event - POI 527656_11 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20168 | 165.04 | Potential P4 Event - POI 527656_13 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20168 | 165.04 | Potential P4 Event - POI 527656_14 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20192 | 165.64 | Potential P4 Event - POI 527656_0 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.202 | 164.89 | Potential P4 Event - POI 527656_10 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21015 | 109.73 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21015 | 110.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20042 | 124.23 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20447 | 138.42 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 128.24 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 131.95 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 135.41 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 135.88 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 138.79 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 139.6 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 139.63 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 140.37 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 119.52 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 119.53 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29756 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28714 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.01 | P11:25:EES:WATERF:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.01 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.01 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22324 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22435 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22435 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22435 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2245 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2245 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22456 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22456 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22469 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22474 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22595 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22628 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22629 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22646 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22651 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22685 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22685 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22783 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22816 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22825 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22841 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22847 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22848 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2301 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23078 | 107.18 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23083 | 106.47 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23083 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2319 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23285 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24205 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25113 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25198 | 104.54 | Potential P4 Event - POI 527656_13 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2663 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38265 | 154.86 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41996 | 188.13 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4214 | 187.42 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 183.57 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 183.59 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 195.61 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22208 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24432 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38232 | 155.38 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41955 | 188.56 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42097 | 187.81 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 184.02 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 184.11 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 196.06 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20042 | 124.63 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20447 | 141.25 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 130.11 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 134.46 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 137.98 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 138.46 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 141.54 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 142.35 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 142.4 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 143.16 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 118.53 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 120.63 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 120.63 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29756 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28714 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21277 | 162.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21277 | 164.73 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21277 | 164.73 | Potential P4 Event - POI 527656_11 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21277 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21291 | 165.04 | Potential P4 Event - POI 527656_13 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21291 | 165.04 | Potential P4 Event - POI 527656_14 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21326 | 165.64 | Potential P4 Event - POI 527656_0 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21354 | 164.89 | Potential P4 Event - POI 527656_10 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.20565 | 109.73 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.20565 | 110.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20457 | 119.52 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20457 | 119.53 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.27946 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.26967 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2149 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21745 | 100.01 | P11:25:EES:WATERF:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21745 | 100.01 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21745 | 100.01 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21745 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21745 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21745 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21745 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21745 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21745 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21745 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21745 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21745 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21745 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21745 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21889 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21889 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2189 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21905 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21905 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21911 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21911 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21928 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21929 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2205 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22073 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22098 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22099 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22102 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22107 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22107 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22273 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22282 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22298 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22303 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22304 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22404 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22433 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2247 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22535 | 107.18 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22541 | 106.47 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22541 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22763 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23757 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24506 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.246 | 104.54 | Potential P4 Event - POI 527656_13 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26795 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.36755 | 154.86 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41012 | 188.13 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41112 | 187.42 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41468 | 183.57 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41468 | 183.59 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41468 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41468 | 195.61 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21797 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24584 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.36723 | 155.38 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.40972 | 188.56 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41071 | 187.81 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41425 | 184.02 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41425 | 184.11 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41425 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41425 | 196.06 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20457 | 118.53 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20457 | 120.63 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20457 | 120.63 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.27946 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.26967 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2111 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2425 | 154.86 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26426 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.30892 | 187.42 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31108 | 183.57 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31108 | 183.59 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31108 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31108 | 195.61 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31204 | 188.13 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24229 | 155.38 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24246 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.30861 | 187.81 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31076 | 184.02 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31076 | 184.11 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31076 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31076 | 196.06 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31174 | 188.56 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22797 | 162.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22797 | 164.73 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22797 | 164.73 | Potential P4 Event - POI 527656_11 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22797 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22811 | 165.04 | Potential P4 Event - POI 527656_13 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22811 | 165.04 | Potential P4 Event - POI 527656_14 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22841 | 165.64 | Potential P4 Event - POI 527656_0 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.2286 | 164.89 | Potential P4 Event - POI 527656_10 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.22751 | 109.73 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.22751 | 110.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20069 | 128.24 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20069 | 131.95 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20069 | 135.41 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20069 | 135.88 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20069 | 138.79 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20069 | 139.6 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20069 | 139.63 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20069 | 140.37 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21243 | 119.52 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21243 | 119.53 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.28614 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.27612 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21856 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22018 | 100.01 | P11:25:EES:WATERF:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22018 | 100.01 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22018 | 100.01 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22018 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22018 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22018 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22018 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22018 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22018 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22018 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22018 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22018 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22018 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22018 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22162 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22162 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22162 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22176 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22176 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22183 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22183 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22199 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22201 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22322 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22341 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22366 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22367 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22374 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22375 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22375 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22544 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22552 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22569 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22574 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22575 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22624 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22668 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22735 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22805 | 107.18 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22811 | 106.47 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22811 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23026 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24004 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25072 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25165 | 104.54 | Potential P4 Event - POI 527656_13 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26999 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37384 | 154.86 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41505 | 188.13 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41626 | 187.42 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41988 | 183.57 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41988 | 183.59 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41988 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41988 | 195.61 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22023 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24771 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37352 | 155.38 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41465 | 188.56 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41583 | 187.81 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41945 | 184.02 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41945 | 184.11 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41945 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41945 | 196.06 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20069 | 130.11 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20069 | 134.46 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20069 | 137.98 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20069 | 138.46 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20069 | 141.54 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20069 | 142.35 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20069 | 142.4 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20069 | 143.16 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21243 | 118.53 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21243 | 120.63 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21243 | 120.63 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.28614 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.27612 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20322 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21022 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26899 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26934 | 154.86 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34984 | 187.42 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.35135 | 188.13 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.35255 | 183.57 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.35255 | 183.59 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.35255 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.35255 | 195.61 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2468 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2691 | 155.38 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.34949 | 187.81 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.35101 | 188.56 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.35219 | 184.02 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.35219 | 184.11 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.35219 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.35219 | 196.06 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21414 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21646 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21677 | 104.54 | Potential P4 Event - POI 527656_13 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21765 | 100.01 | P11:25:EES:WATERF:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21765 | 100.01 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21765 | 100.01 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21765 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21765 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21765 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21765 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21765 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21765 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21765 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21765 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21765 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21765 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21765 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21907 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21908 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21908 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21922 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21922 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2193 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2193 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21946 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2195 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21964 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21999 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21999 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22065 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2207 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22123 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22136 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22137 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22287 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22296 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22312 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22317 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22318 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2246 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22547 | 107.18 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22553 | 106.47 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22553 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22797 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23632 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2392 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28822 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31335 | 154.86 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41059 | 188.13 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4115 | 187.42 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41505 | 183.57 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41505 | 183.59 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41505 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41505 | 195.61 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21946 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.26444 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31307 | 155.38 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41019 | 188.56 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41109 | 187.81 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41463 | 184.02 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41463 | 184.11 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41463 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41463 | 196.06 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40427 | 188.65 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40667 | 139.38 | Potential P4 Event - POI 515458_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40708 | 139.3 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40789 | 137.63 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40802 | 133.93 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40867 | 136.02 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4093 | 138.87 | Potential P4 Event - POI 773600_4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40932 | 138.88 | Potential P4 Event - POI 773600_7 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40932 | 138.88 | Potential P4 Event - POI 773600_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40935 | 132.94 | P23:345:WERE:JEC-345-16:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40935 | 133 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40936 | 133.01 | P23:345:WERE:JEC-345-20:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40938 | 132.62 | 514796 IODINE-4 138 515376 WWRDEHV4 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40938 | 132.62 | 514796 IODINE-4 138 515533 REDCLFT4 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40938 | 132.82 | 532792 FR2EAST7 345 588364 G16-153-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40938 | 132.87 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40939 | 132.92 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4094 | 132.81 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4094 | 132.83 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4094 | 132.85 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40941 | 132.88 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40941 | 132.88 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40942 | 133.45 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.45 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.59 | 659387 KUMMERDG-BE3 345 659390 PATENTGT-BE3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.61 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.81 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.81 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.84 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.84 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.84 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.86 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.9 | P13:230,22:CLEC::G3MADISN::1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.9 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.93 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.94 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.95 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.96 | ASGI-2023-001_POI_528252_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.96 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.96 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.96 | P23:500:EES-EAI:DELL:B8320::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.98 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.99 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.99 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.99 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 132.99 | P11:115:XEL:HBR #6 7 8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133 | P12:EHV:EES::8ISES%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133 | P23:345:XEL:8H14 PRI | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133 | P23:345:XEL:8H17 PRI AS | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.01 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.01 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.04 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.04 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.05 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.05 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.05 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.06 | P11:21:EES:RVB:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.06 | P11:HV:EES::1RVR_BND_G1!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.06 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.06 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.06 | P23:345:MEC:LOUISA 964 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.07 | P23:345:XEL:8N22 SHC | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.09 | P11:25:EES:WATERF:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.09 | P11:HV:EES::1WAT U3!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.09 | P13:230:EES:WATERF:T6:T7 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.09 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.09 | P23:345:MEC:CBEC 908 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.1 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.11 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.11 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.11 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.11 | P23:345:MEC:CBEC 905 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.15 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.18 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.19 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.19 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.21 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.28 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.3 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 133.47 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.76 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.88 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.24 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.42 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.43 | GEN-2023-201_POI_776000_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.91 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.91 | GEN-2023-236_POI_776700_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 138.67 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 138.67 | GEN-2023-081_POI_773600_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40944 | 132.91 | P12:069:GLHP:COLE-TURPIN-BEARD-ADAMS-JEFFERSON:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40944 | 133.04 | P23:500:EES-EAI:INDEP2:B6126 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40953 | 133.26 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40958 | 133.29 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40967 | 133.51 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40968 | 133.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40978 | 133.56 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40979 | 133.29 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40981 | 133.57 | P42:345:OKGE:SB_SEOL7385:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40986 | 133.2 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40987 | 133.33 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41005 | 133.61 | P42:345:OKGE:SB_BAER7318:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41005 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41005 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41074 | 135.99 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.411 | 136.22 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.411 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.411 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41216 | 134.9 | P13:69-138:AEPW:SHAM 2WT:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41216 | 134.91 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41216 | 135.3 | P13:69-115:AEPW:SHAM 2WT:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41216 | 135.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41256 | 137.34 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41339 | 138.51 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41378 | 163.83 | Potential P4 Event - POI 527656_0 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41414 | 163.21 | Potential P4 Event - POI 527656_13 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41414 | 163.21 | Potential P4 Event - POI 527656_14 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41422 | 161.82 | Potential P4 Event - POI 527656_9 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41428 | 138.61 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41437 | 161.31 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41437 | 161.31 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41437 | 164.87 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41437 | 164.87 | Potential P4 Event - POI 527656_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41559 | 140.79 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41906 | 137.06 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.46082 | 163.65 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4623 | 157.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4623 | 157.17 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4623 | 157.17 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40427 | 190.26 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40667 | 141.48 | Potential P4 Event - POI 515458_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40708 | 142.25 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40789 | 138.3 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40802 | 135.66 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40867 | 137.76 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40907 | 134.6 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4093 | 142.83 | Potential P4 Event - POI 773600_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40932 | 142.91 | Potential P4 Event - POI 773600_7 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40932 | 142.91 | Potential P4 Event - POI 773600_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40935 | 134.9 | P23:345:WERE:JEC-345-16:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40935 | 134.92 | P13:345:OPPD:NEBCTY2G:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40936 | 134.93 | P23:345:WERE:JEC-345-20:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40937 | 134.94 | P11:345:WERE:JECU3-GEN:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40938 | 134.63 | 514787 DEWEY 4 138 515533 REDCLFT4 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40938 | 134.83 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40939 | 134.63 | 514789 MENOTAP4 138 514790 IMO 4 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40939 | 134.82 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4094 | 134.83 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40941 | 134.83 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40941 | 134.83 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40942 | 135.25 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.3 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.64 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.82 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.82 | P11:EHV:EES::1FRNTR 1!:1(1) | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.83 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.83 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.86 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.87 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.89 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.92 | P11:115:XEL:HBR #6 7 8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.92 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.92 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.93 | P13:345,24:CLEC::G1DOLHILL::1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.93 | P23:345:XEL:8H14 PRI | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.93 | P23:345:XEL:8H17 PRI AS | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.94 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.94 | P13:230,22:CLEC::G3MADISN::1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.95 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.96 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.96 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.96 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.96 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.97 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.97 | P23:345:XEL:8N22 SHC | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.97 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.98 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.98 | P23:345:MEC:LOUISA 964 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.99 | P23:345:MEC:CBEC 905 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 134.99 | P23:345:MEC:LOUISA 954 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.01 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.02 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.02 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.02 | P23:500:EES-EAI:WH_BLF:B7942 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.03 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.03 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.04 | P11:26:EES-EAI:INDEP2:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.04 | P11:26:EES-EAI:INDEP2:1:D401 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.04 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.04 | P11:EHV:EES::1ISES U2:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.04 | P11:HV:EES::1ISES U1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.05 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.05 | P12:EHV:EES::8ANO%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.05 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.06 | ASGI-2021-001_POI_766031_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.06 | ASGI-2023-001_POI_528252_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.06 | P11:22:EES-EAI:ARK_NU:1:D395 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.06 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.07 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.09 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.09 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.1 | P11:21:EES:RVB:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.11 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.11 | P11:EHV:EES::1ANO U2:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.14 | P11:25:EES:WATERF:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.14 | P11:HV:EES::1WAT U3!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.14 | P13:230:EES:WATERF:T6:T7 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.21 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.23 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.27 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 135.34 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 137.63 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 137.79 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 137.99 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 138.62 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 138.62 | GEN-2023-201_POI_776000_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 139.4 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 139.4 | GEN-2023-236_POI_776700_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 142.7 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40943 | 142.7 | GEN-2023-081_POI_773600_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40944 | 134.97 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40967 | 135.31 | P42:345:OKGE:SB_BVTY7387:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40967 | 135.72 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40968 | 135.59 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40978 | 135.28 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40979 | 135.05 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40986 | 134.98 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40987 | 135.19 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41005 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41005 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41005 | 135.54 | P42:345:OKGE:SB_BAER7318:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41074 | 138.08 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.411 | 137.62 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.411 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.411 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41216 | 136.85 | P13:69-138:AEPW:SHAM 2WT:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41216 | 136.86 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41216 | 137.23 | P13:69-115:AEPW:SHAM 2WT:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41216 | 137.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41256 | 139.06 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41339 | 140.57 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41378 | 167.97 | Potential P4 Event - POI 527656_0 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41414 | 167.9 | Potential P4 Event - POI 527656_13 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41414 | 167.9 | Potential P4 Event - POI 527656_14 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4142 | 166.55 | Potential P4 Event - POI 527656_10 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41428 | 140.18 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41437 | 165.89 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41437 | 165.89 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41437 | 169.93 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41437 | 169.93 | Potential P4 Event - POI 527656_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41559 | 142.88 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.41906 | 139.08 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.46082 | 165.72 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4623 | 159.05 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4623 | 159.06 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4623 | 159.06 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22679 | 154.86 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2497 | 187.42 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25111 | 183.57 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25111 | 183.59 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25111 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25111 | 195.61 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25435 | 188.13 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22659 | 155.38 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24944 | 187.81 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25085 | 184.02 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25085 | 184.11 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25085 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25085 | 196.06 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25411 | 188.56 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.38875 | 188.65 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3888 | 139.38 | Potential P4 Event - POI 515458_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.38886 | 139.3 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.38981 | 137.63 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.38982 | 133.93 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39042 | 136.02 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39085 | 138.87 | Potential P4 Event - POI 773600_4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39087 | 138.88 | Potential P4 Event - POI 773600_7 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39087 | 138.88 | Potential P4 Event - POI 773600_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39089 | 132.94 | P23:345:WERE:JEC-345-16:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39089 | 133 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3909 | 133.01 | P23:345:WERE:JEC-345-20:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39092 | 132.62 | 514796 IODINE-4 138 515376 WWRDEHV4 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39092 | 132.62 | 514796 IODINE-4 138 515533 REDCLFT4 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39092 | 132.82 | 532792 FR2EAST7 345 588364 G16-153-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39092 | 132.87 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39093 | 132.92 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39094 | 132.81 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39094 | 132.83 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39094 | 132.85 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39094 | 132.88 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39094 | 132.88 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39095 | 133.45 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39096 | 132.84 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.45 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.59 | 659387 KUMMERDG-BE3 345 659390 PATENTGT-BE3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.61 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.81 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.81 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.84 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.84 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.86 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.9 | P13:230,22:CLEC::G3MADISN::1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.9 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.91 | P12:069:GLHP:COLE-TURPIN-BEARD-ADAMS-JEFFERSON:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.93 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.94 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.95 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.96 | ASGI-2023-001_POI_528252_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.96 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.96 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.96 | P23:500:EES-EAI:DELL:B8320::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.98 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.99 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.99 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.99 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 132.99 | P11:115:XEL:HBR #6 7 8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133 | P12:EHV:EES::8ISES%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133 | P23:345:XEL:8H14 PRI | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133 | P23:345:XEL:8H17 PRI AS | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.01 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.01 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.04 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.04 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.04 | P23:500:EES-EAI:INDEP2:B6126 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.05 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.05 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.05 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.06 | P11:21:EES:RVB:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.06 | P11:HV:EES::1RVR_BND_G1!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.06 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.06 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.06 | P23:345:MEC:LOUISA 964 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.07 | P23:345:XEL:8N22 SHC | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.09 | P11:25:EES:WATERF:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.09 | P11:HV:EES::1WAT U3!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.09 | P13:230:EES:WATERF:T6:T7 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.09 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.09 | P23:345:MEC:CBEC 908 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.1 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.11 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.11 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.11 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.11 | P23:345:MEC:CBEC 905 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.15 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.18 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.19 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.19 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.21 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.28 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.3 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 133.47 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.76 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.88 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.24 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.42 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.43 | GEN-2023-201_POI_776000_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.91 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.91 | GEN-2023-236_POI_776700_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 138.67 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 138.67 | GEN-2023-081_POI_773600_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39107 | 133.26 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39111 | 133.29 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3912 | 133.51 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39121 | 133.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39133 | 133.29 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39134 | 133.56 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39138 | 133.57 | P42:345:OKGE:SB_SEOL7385:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39139 | 133.33 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3914 | 133.2 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39157 | 133.61 | P42:345:OKGE:SB_BAER7318:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39161 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39161 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39242 | 135.99 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3926 | 136.22 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3926 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3926 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39345 | 134.9 | P13:69-138:AEPW:SHAM 2WT:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39345 | 134.91 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39345 | 135.3 | P13:69-115:AEPW:SHAM 2WT:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39345 | 135.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39399 | 137.34 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39555 | 138.51 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39626 | 138.61 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39769 | 140.79 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39772 | 163.83 | Potential P4 Event - POI 527656_0 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39799 | 163.21 | Potential P4 Event - POI 527656_13 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39799 | 163.21 | Potential P4 Event - POI 527656_14 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39801 | 161.82 | Potential P4 Event - POI 527656_9 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39816 | 161.31 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39816 | 161.31 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39816 | 164.87 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39816 | 164.87 | Potential P4 Event - POI 527656_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40009 | 137.06 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.43954 | 163.65 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.44102 | 157.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.44102 | 157.17 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.44102 | 157.17 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.38875 | 190.26 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3888 | 141.48 | Potential P4 Event - POI 515458_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.38886 | 142.25 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.38981 | 138.3 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.38982 | 135.66 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39042 | 137.76 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39061 | 134.6 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39085 | 142.83 | Potential P4 Event - POI 773600_1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39087 | 142.91 | Potential P4 Event - POI 773600_7 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39087 | 142.91 | Potential P4 Event - POI 773600_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39089 | 134.9 | P23:345:WERE:JEC-345-16:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39089 | 134.92 | P13:345:OPPD:NEBCTY2G:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3909 | 134.93 | P23:345:WERE:JEC-345-20:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39091 | 134.94 | P11:345:WERE:JECU3-GEN:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39092 | 134.63 | 514787 DEWEY 4 138 515533 REDCLFT4 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39092 | 134.63 | 514789 MENOTAP4 138 514790 IMO 4 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39092 | 134.83 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39093 | 134.82 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39094 | 134.83 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39094 | 134.83 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39094 | 134.83 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39095 | 135.25 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39096 | 134.82 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.3 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.64 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.82 | P11:EHV:EES::1FRNTR 1!:1(1) | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.83 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.83 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.86 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.87 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.89 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.92 | P11:115:XEL:HBR #6 7 8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.92 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.92 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.93 | P13:345,24:CLEC::G1DOLHILL::1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.93 | P23:345:XEL:8H14 PRI | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.93 | P23:345:XEL:8H17 PRI AS | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.94 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.94 | P13:230,22:CLEC::G3MADISN::1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.95 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.96 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.96 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.96 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.96 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.97 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.97 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.97 | P23:345:XEL:8N22 SHC | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.97 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.98 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.98 | P23:345:MEC:LOUISA 964 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.99 | P23:345:MEC:CBEC 905 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 134.99 | P23:345:MEC:LOUISA 954 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.01 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.02 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.02 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.02 | P23:500:EES-EAI:WH_BLF:B7942 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.03 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.03 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.04 | P11:26:EES-EAI:INDEP2:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.04 | P11:26:EES-EAI:INDEP2:1:D401 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.04 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.04 | P11:EHV:EES::1ISES U2:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.04 | P11:HV:EES::1ISES U1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.05 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.05 | P12:EHV:EES::8ANO%:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.05 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.06 | ASGI-2021-001_POI_766031_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.06 | ASGI-2023-001_POI_528252_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.06 | P11:22:EES-EAI:ARK_NU:1:D395 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.06 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.07 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.09 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.09 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.1 | P11:21:EES:RVB:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.11 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.11 | P11:EHV:EES::1ANO U2:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.14 | P11:25:EES:WATERF:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.14 | P11:HV:EES::1WAT U3!:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.14 | P13:230:EES:WATERF:T6:T7 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.21 | P12:EHV:EES::7CALAWY 1:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.23 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.27 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 135.34 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 137.63 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 137.79 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 137.99 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 138.62 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 138.62 | GEN-2023-201_POI_776000_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 139.4 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 139.4 | GEN-2023-236_POI_776700_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 142.7 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39097 | 142.7 | GEN-2023-081_POI_773600_Generator_outage | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3912 | 135.31 | P42:345:OKGE:SB_BVTY7387:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3912 | 135.72 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39121 | 135.59 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39133 | 135.05 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39134 | 135.28 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39139 | 135.19 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3914 | 134.98 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39157 | 135.54 | P42:345:OKGE:SB_BAER7318:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39161 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39161 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39242 | 138.08 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3926 | 137.62 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3926 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3926 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39345 | 136.85 | P13:69-138:AEPW:SHAM 2WT:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39345 | 136.86 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39345 | 137.23 | P13:69-115:AEPW:SHAM 2WT:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39345 | 137.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39399 | 139.06 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39555 | 140.57 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39626 | 140.18 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39769 | 142.88 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39772 | 167.97 | Potential P4 Event - POI 527656_0 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39799 | 167.9 | Potential P4 Event - POI 527656_13 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39799 | 167.9 | Potential P4 Event - POI 527656_14 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39807 | 166.55 | Potential P4 Event - POI 527656_10 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39816 | 165.89 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39816 | 165.89 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39816 | 169.93 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39816 | 169.93 | Potential P4 Event - POI 527656_8 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40009 | 139.08 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.43954 | 165.72 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.44102 | 159.05 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.44102 | 159.06 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.44102 | 159.06 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24495 | 154.86 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26748 | 187.42 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26913 | 183.57 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26913 | 183.59 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26913 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26913 | 195.61 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.27151 | 188.13 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24473 | 155.38 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.26721 | 187.81 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.26886 | 184.02 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.26886 | 184.11 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.26886 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.26886 | 196.06 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.27125 | 188.56 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20064 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20073 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20089 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20095 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20096 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20277 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20331 | 107.18 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20337 | 106.47 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20337 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20643 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21704 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21945 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.27646 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.27833 | 154.86 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28914 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.36936 | 187.42 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37011 | 188.13 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37234 | 183.57 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37234 | 183.59 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37234 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37234 | 195.61 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.20134 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25365 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.27808 | 155.38 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.36899 | 187.81 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.36975 | 188.56 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37195 | 184.02 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37195 | 184.11 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37195 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37195 | 196.06 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27L | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 1 | 145.27 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27L | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 1 | 144.13 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27L | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.24742 | 100.21 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27L | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.24742 | 100.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24471 | 152.61 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26251 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31198 | 183.79 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.3142 | 179.87 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.3142 | 179.92 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.3142 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.3142 | 191.94 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31486 | 184.51 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24085 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24449 | 153.1 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31167 | 184.16 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31388 | 180.34 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31388 | 180.35 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31388 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31388 | 192.34 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31456 | 184.91 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20251 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20444 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20556 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20789 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20799 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20815 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2082 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20821 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20825 | 101.44 | Potential P4 Event - POI 523823_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20978 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21058 | 104.75 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21064 | 104.09 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21064 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21334 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22576 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.27825 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.29449 | 152.61 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.383 | 183.79 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38309 | 184.51 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38618 | 179.87 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38618 | 179.92 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38618 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38618 | 191.94 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.20713 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25529 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.29424 | 153.1 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38261 | 184.16 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38271 | 184.91 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38578 | 180.34 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38578 | 180.35 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38578 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38578 | 192.34 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-001 | FROM->TO | 528413 TAYLOR 3 115 528449 W_BENDER 3 115 1 | 143 | 157 | 1 | 136.32 | 528355 MADDOX 3 115 762442 G18-004-TAP 115 1 | TDF Impact | Rebuild the existing TAYLOR3 to W_BENDER3 115 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20014 | 165.4 | Potential P4 Event - POI 527656_0 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.2073 | 114.05 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.2073 | 114.9 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20217 | 136.58 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 126.41 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 130.57 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 133.59 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 134.05 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 136.94 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 137.75 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 137.78 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 138.96 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 116.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 119.14 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 119.15 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2936 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28327 | 175.43 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2206 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22083 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2236 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22378 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22589 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.226 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22616 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22621 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22622 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22626 | 101.44 | Potential P4 Event - POI 523823_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22771 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22855 | 104.75 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22861 | 104.09 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22861 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23058 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24019 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24771 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26243 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37835 | 152.61 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41566 | 184.51 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41702 | 183.79 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 179.87 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 179.92 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 191.94 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22037 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24078 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37802 | 153.1 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41526 | 184.91 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4166 | 184.16 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 180.34 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 180.35 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 192.34 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20217 | 139.23 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 127.99 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 132.76 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 135.94 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 136.42 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 139.53 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 140.37 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 140.41 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 141.59 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 117.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 120.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 120.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2936 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28327 | 175.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.28139 | 112.47 | GEN-2023-237_POI_560022_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35005 | 136.58 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35169 | 126.41 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35169 | 130.57 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35169 | 133.59 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35169 | 134.05 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35169 | 136.94 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35169 | 137.75 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35169 | 137.78 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35169 | 138.96 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35645 | 108.23 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35645 | 108.23 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35662 | 107.69 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35662 | 107.69 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35664 | 108.08 | P23:500:EES:PERRYVILLE:R7372::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35665 | 107.69 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.35 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.38 | P23:345:XEL:8N17 SHC | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.39 | P23:345:XEL:8N22 SHC | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.4 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.4 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.4 | P23:345:XEL:8N8 MNN | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.6 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.67 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.69 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.84 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.85 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.86 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.88 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.88 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.02 | P13:138:EES:LC:T1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.02 | P13:138:EES:LC:T2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.08 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.1 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.1 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.1 | P11:EHV:EES::1FRNTR 1!:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.12 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.15 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.15 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.19 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.2 | P13:230,22:CLEC::G2RODEMR::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.23 | P23:500:EES:PERRYVILLE:R3779::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.25 | P11:18:EES:NINEMI:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.34 | P13:230,22:CLEC::G3MADISN::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.35 | P11:HV:EES::1ISES U1:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.36 | P11:EHV:EES::1ISES U2:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.36 | P13:230:EES:NINEMI:AT4 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.37 | P11:26:EES:NINEMI:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.37 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.37 | P13:230:EES:NINEMI:AT5 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.38 | P11:22:CLEC:RODEMR1:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.39 | P11:26:EES:NINEMI:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.39 | P11:HV:EES::1NMIL U5!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.42 | P12:EHV:EES::8WHT BLUFF%:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.42 | P13:500:EES-EAI:WH_BLF:ST2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.43 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.44 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.45 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.5 | P13:345,24:CLEC::G1DOLHILL::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.55 | P12:EHV:EES::8ANO%:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.59 | P11:22:EES-EAI:ARK_NU:1:D395 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.67 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.67 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.69 | P11:21:EES:RVB:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.69 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.69 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.71 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.71 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.73 | P11:HV:EES::1LEWIS_U3 ST:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.78 | P11:25:EES:WATERF:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.78 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.78 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.91 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.91 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.91 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.96 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.97 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.99 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 109.92 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 109.95 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 110.21 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 110.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 112.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35671 | 107.69 | P13:345:OPPD:NEBCTY2G:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35671 | 107.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35671 | 107.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35671 | 107.91 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35672 | 107.91 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35672 | 108.02 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35672 | 108.03 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35673 | 107.96 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35674 | 108.11 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35674 | 108.11 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35675 | 107.18 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35679 | 107.98 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35683 | 108.21 | P23:345:WERE:WICH-345-50:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35683 | 108.41 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35692 | 108.21 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35692 | 108.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.357 | 108.27 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35706 | 108.64 | P23:345:WERE:BUFF-345-534:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35706 | 108.64 | P23:345:WERE:BUFF-345-543:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35735 | 110.01 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35736 | 109.29 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35746 | 109.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35746 | 109.68 | P23:345:SUNC:BU_BRK488:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35754 | 109.95 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35754 | 109.95 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35755 | 109.91 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3576 | 110.26 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3576 | 110.27 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35768 | 109.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35768 | 109.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35781 | 112.06 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.358 | 110.39 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35808 | 111.18 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35808 | 111.18 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35854 | 111 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35886 | 110.36 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35919 | 115.01 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35967 | 114.56 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35975 | 114.62 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3599 | 114.95 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3599 | 114.95 | Potential P4 Event - POI 531449_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36059 | 115.82 | POI 515800_22 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36059 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36203 | 120.81 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36203 | 121.59 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36709 | 116.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36709 | 119.14 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36709 | 119.15 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36725 | 121.87 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.59062 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30506 | 119.03 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30649 | 110.17 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30649 | 113.79 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30649 | 116.43 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30649 | 116.82 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30649 | 119.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30649 | 120.05 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30649 | 120.08 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30649 | 121.11 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31302 | 100.23 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31364 | 100.18 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31364 | 100.18 | Potential P4 Event - POI 531449_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31424 | 100.94 | POI 515800_22 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31424 | 101.06 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31549 | 105.29 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31549 | 105.97 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3199 | 101.8 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3199 | 103.84 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3199 | 103.84 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.32004 | 106.21 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.56984 | 175.43 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23155 | 100.95 | GEN-2023-237_POI_560022_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33895 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34033 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34169 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34251 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34321 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34333 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34349 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34354 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34354 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34358 | 101.44 | Potential P4 Event - POI 523823_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34465 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34537 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34547 | 104.75 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34551 | 104.09 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34551 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34695 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34698 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.3614 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.62977 | 184.51 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.6397 | 183.79 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.64637 | 179.87 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.64637 | 179.92 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.64637 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.64637 | 191.94 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.65511 | 152.61 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31835 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.33158 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.62915 | 184.91 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.63905 | 184.16 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.6457 | 180.34 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.6457 | 180.35 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.6457 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.6457 | 192.34 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.65453 | 153.1 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.28139 | 113.2 | GEN-2023-237_POI_560022_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35005 | 139.23 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35169 | 127.99 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35169 | 132.76 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35169 | 135.94 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35169 | 136.42 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35169 | 139.53 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35169 | 140.37 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35169 | 140.41 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35169 | 141.59 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35645 | 108.46 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35645 | 108.46 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35662 | 107.93 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35662 | 107.93 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35664 | 108.31 | P23:500:EES:PERRYVILLE:R7372::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35665 | 107.93 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.6 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.64 | P23:345:XEL:8N17 SHC | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.64 | P23:345:XEL:8N22 SHC | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.65 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.65 | P23:345:XEL:8N8 MNN | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.84 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.91 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.93 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.93 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 107.93 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.08 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.09 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.1 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.14 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.14 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.24 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.26 | P13:138:EES:LC:T1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.26 | P13:138:EES:LC:T2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.31 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.33 | P11:EHV:EES::1FRNTR 1!:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.34 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.34 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.36 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.38 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.38 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.43 | P13:230,22:CLEC::G2RODEMR::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.43 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.47 | P23:500:EES:PERRYVILLE:R3779::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.48 | P11:18:EES:NINEMI:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.57 | P13:230,22:CLEC::G3MADISN::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.58 | P11:HV:EES::1ISES U1:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.59 | P11:EHV:EES::1ISES U2:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.59 | P13:230:EES:NINEMI:AT4 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.6 | P11:26:EES:NINEMI:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.6 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.6 | P13:230:EES:NINEMI:AT5 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.61 | P11:22:CLEC:RODEMR1:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.62 | P11:26:EES:NINEMI:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.62 | P11:HV:EES::1NMIL U5!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.65 | P12:EHV:EES::8WHT BLUFF%:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.65 | P13:500:EES-EAI:WH_BLF:ST2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.66 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.67 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.69 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.73 | P13:345,24:CLEC::G1DOLHILL::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.78 | P12:EHV:EES::8ANO%:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.82 | P11:22:EES-EAI:ARK_NU:1:D395 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.9 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.9 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.92 | P11:21:EES:RVB:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.94 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.94 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 108.96 | P11:HV:EES::1LEWIS_U3 ST:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 109 | P11:25:EES:WATERF:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 109 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 109.01 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 109.26 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 109.26 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 109.26 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 109.33 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 109.33 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 109.38 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 110.13 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 110.7 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35666 | 113.2 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35671 | 108.15 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35672 | 108.15 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35672 | 108.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35672 | 108.27 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35673 | 108.2 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35674 | 108.34 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35674 | 108.34 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35675 | 107.43 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35675 | 107.43 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35679 | 108.22 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35683 | 108.44 | P23:345:WERE:WICH-345-50:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35683 | 108.64 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35692 | 108.38 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35692 | 108.38 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB :::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35698 | 110.28 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.357 | 108.5 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35706 | 108.87 | P23:345:WERE:BUFF-345-534:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35706 | 108.87 | P23:345:WERE:BUFF-345-543:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35735 | 110.2 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35736 | 109.48 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35746 | 109.88 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35746 | 109.88 | P23:345:SUNC:BU_BRK488:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35754 | 110.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35754 | 110.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35755 | 110.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3576 | 110.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3576 | 110.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35768 | 109.68 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35768 | 109.73 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35781 | 112.33 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.358 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.358 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35808 | 111.45 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35808 | 111.45 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35854 | 111.12 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35886 | 110.52 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35919 | 115.2 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35967 | 114.65 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35975 | 114.7 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3599 | 115.03 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3599 | 115.03 | Potential P4 Event - POI 531449_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36059 | 115.8 | POI 515800_22 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36059 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36203 | 121.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36203 | 121.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36709 | 117.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36709 | 120.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36709 | 120.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36725 | 122.24 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.59062 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30506 | 121.34 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30649 | 111.55 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30649 | 115.7 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30649 | 118.48 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30649 | 118.89 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30649 | 121.6 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30649 | 122.33 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30649 | 122.37 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30649 | 123.4 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31302 | 100.4 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31364 | 100.26 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31364 | 100.26 | Potential P4 Event - POI 531449_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31424 | 100.92 | POI 515800_22 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31424 | 101.05 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31549 | 105.57 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31549 | 106.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3199 | 102.67 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3199 | 104.7 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3199 | 104.7 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.32004 | 106.54 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.56984 | 175.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20014 | 165.4 | Potential P4 Event - POI 527656_0 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.2073 | 114.05 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.2073 | 114.9 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20217 | 136.58 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 126.41 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 130.57 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 133.59 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 134.05 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 136.94 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 137.75 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 137.78 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 138.96 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 116.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 119.14 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 119.15 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2936 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28327 | 175.43 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2206 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22083 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2236 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22378 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22589 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.226 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22616 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22621 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22622 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22626 | 101.44 | Potential P4 Event - POI 523823_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22771 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22855 | 104.75 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22861 | 104.09 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22861 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23058 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24019 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24771 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26243 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37835 | 152.61 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41566 | 184.51 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41702 | 183.79 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 179.87 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 179.92 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 191.94 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22037 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24078 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37802 | 153.1 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41526 | 184.91 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4166 | 184.16 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 180.34 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 180.35 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 192.34 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20217 | 139.23 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 127.99 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 132.76 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 135.94 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 136.42 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 139.53 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 140.37 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 140.41 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 141.59 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 117.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 120.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 120.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2936 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28327 | 175.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20021 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25825 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25903 | 152.61 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.32883 | 183.79 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33104 | 184.51 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33128 | 179.87 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33128 | 179.92 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33128 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33128 | 191.94 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23694 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2588 | 153.1 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.32849 | 184.16 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.33071 | 184.91 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.33093 | 180.34 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.33093 | 180.35 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.33093 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.33093 | 192.34 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20498 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26003 | 152.61 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28405 | 183.79 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28594 | 179.87 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28594 | 179.92 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28594 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28594 | 191.94 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28758 | 184.51 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2598 | 153.1 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.28377 | 184.16 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.28564 | 180.34 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.28564 | 180.35 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.28564 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.28564 | 192.34 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2873 | 184.91 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20498 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21697 | 108.23 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21697 | 108.23 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21715 | 107.69 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21715 | 107.69 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21717 | 107.69 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21717 | 108.08 | P23:500:EES:PERRYVILLE:R7372::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.35 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.38 | P23:345:XEL:8N17 SHC | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.39 | P23:345:XEL:8N22 SHC | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.4 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.4 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.4 | P23:345:XEL:8N8 MNN | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.6 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.67 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.69 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.84 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.85 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.86 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.88 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.88 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.02 | P13:138:EES:LC:T1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.02 | P13:138:EES:LC:T2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.08 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.1 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.1 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.1 | P11:EHV:EES::1FRNTR 1!:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.12 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.15 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.15 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.19 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.2 | P13:230,22:CLEC::G2RODEMR::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.23 | P23:500:EES:PERRYVILLE:R3779::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.25 | P11:18:EES:NINEMI:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.34 | P13:230,22:CLEC::G3MADISN::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.35 | P11:HV:EES::1ISES U1:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.36 | P11:EHV:EES::1ISES U2:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.36 | P13:230:EES:NINEMI:AT4 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.37 | P11:26:EES:NINEMI:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.37 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.37 | P13:230:EES:NINEMI:AT5 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.38 | P11:22:CLEC:RODEMR1:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.39 | P11:26:EES:NINEMI:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.39 | P11:HV:EES::1NMIL U5!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.42 | P12:EHV:EES::8WHT BLUFF%:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.42 | P13:500:EES-EAI:WH_BLF:ST2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.43 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.44 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.45 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.5 | P13:345,24:CLEC::G1DOLHILL::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.55 | P12:EHV:EES::8ANO%:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.59 | P11:22:EES-EAI:ARK_NU:1:D395 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.67 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.67 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.69 | P11:21:EES:RVB:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.69 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.69 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.71 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.71 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.73 | P11:HV:EES::1LEWIS_U3 ST:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.78 | P11:25:EES:WATERF:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.78 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.78 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.91 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.91 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.91 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.96 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.97 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.99 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 109.92 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 109.95 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 110.21 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 110.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 112.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21723 | 107.69 | P13:345:OPPD:NEBCTY2G:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21723 | 107.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21723 | 107.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21724 | 107.91 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21725 | 107.91 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21726 | 107.96 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21726 | 108.02 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21726 | 108.03 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21727 | 107.18 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21728 | 108.11 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21728 | 108.11 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21736 | 107.98 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2174 | 108.21 | P23:345:WERE:WICH-345-50:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21745 | 108.21 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21745 | 108.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21755 | 108.27 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21757 | 108.41 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21766 | 108.64 | P23:345:WERE:BUFF-345-534:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21766 | 108.64 | P23:345:WERE:BUFF-345-543:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21817 | 110.01 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21818 | 109.95 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21818 | 109.95 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21828 | 109.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21828 | 109.68 | P23:345:SUNC:BU_BRK488:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21833 | 109.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21833 | 109.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21834 | 109.29 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21846 | 109.91 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21922 | 110.26 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21922 | 111 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21923 | 110.27 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21961 | 110.36 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22088 | 114.56 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22096 | 114.62 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22101 | 112.06 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22111 | 114.95 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22111 | 114.95 | Potential P4 Event - POI 531449_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22128 | 111.18 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22128 | 111.18 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2222 | 115.01 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22235 | 110.39 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22364 | 115.82 | POI 515800_22 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22364 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22589 | 121.87 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2274 | 136.58 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22832 | 120.81 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22832 | 121.59 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22847 | 126.41 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22847 | 130.57 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22847 | 133.59 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22847 | 134.05 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22847 | 136.94 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22847 | 137.75 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22847 | 137.78 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22847 | 138.96 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23178 | 116.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23178 | 119.14 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23178 | 119.15 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35965 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20199 | 101.8 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20199 | 103.84 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20199 | 103.84 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.347 | 175.43 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23276 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23373 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23572 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23731 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.238 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2381 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23826 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23831 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23832 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23836 | 101.44 | Potential P4 Event - POI 523823_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23979 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24064 | 104.75 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24069 | 104.09 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24069 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24213 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24396 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24941 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25122 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42557 | 152.61 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.43752 | 184.51 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.43988 | 183.79 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.44386 | 179.87 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.44386 | 179.92 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.44386 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.44386 | 191.94 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22883 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23049 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4252 | 153.1 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.43709 | 184.91 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.43943 | 184.16 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4434 | 180.34 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4434 | 180.35 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4434 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4434 | 192.34 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21697 | 108.46 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21697 | 108.46 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21715 | 107.93 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21715 | 107.93 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21717 | 107.93 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21717 | 108.31 | P23:500:EES:PERRYVILLE:R7372::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.6 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.64 | P23:345:XEL:8N17 SHC | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.64 | P23:345:XEL:8N22 SHC | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.65 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.65 | P23:345:XEL:8N8 MNN | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.84 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.91 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.93 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.93 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 107.93 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.08 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.09 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.1 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.14 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.14 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.24 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.26 | P13:138:EES:LC:T1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.26 | P13:138:EES:LC:T2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.31 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.33 | P11:EHV:EES::1FRNTR 1!:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.34 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.34 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.36 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.38 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.38 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.43 | P13:230,22:CLEC::G2RODEMR::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.43 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.47 | P23:500:EES:PERRYVILLE:R3779::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.48 | P11:18:EES:NINEMI:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.57 | P13:230,22:CLEC::G3MADISN::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.58 | P11:HV:EES::1ISES U1:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.59 | P11:EHV:EES::1ISES U2:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.59 | P13:230:EES:NINEMI:AT4 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.6 | P11:26:EES:NINEMI:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.6 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.6 | P13:230:EES:NINEMI:AT5 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.61 | P11:22:CLEC:RODEMR1:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.62 | P11:26:EES:NINEMI:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.62 | P11:HV:EES::1NMIL U5!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.65 | P12:EHV:EES::8WHT BLUFF%:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.65 | P13:500:EES-EAI:WH_BLF:ST2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.66 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.67 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.69 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.73 | P13:345,24:CLEC::G1DOLHILL::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.78 | P12:EHV:EES::8ANO%:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.82 | P11:22:EES-EAI:ARK_NU:1:D395 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.9 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.9 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.92 | P11:21:EES:RVB:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.94 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.94 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 108.96 | P11:HV:EES::1LEWIS_U3 ST:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 109 | P11:25:EES:WATERF:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 109 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 109.01 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 109.26 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 109.26 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 109.26 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 109.33 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 109.33 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 109.38 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 110.13 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 110.7 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21718 | 113.2 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21724 | 108.15 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21725 | 108.15 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21726 | 108.2 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21726 | 108.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21726 | 108.27 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21727 | 107.43 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21727 | 107.43 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21728 | 108.34 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21728 | 108.34 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21736 | 108.22 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2174 | 108.44 | P23:345:WERE:WICH-345-50:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21745 | 108.38 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21745 | 108.38 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB :::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21755 | 108.5 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21757 | 108.64 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21766 | 108.87 | P23:345:WERE:BUFF-345-534:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21766 | 108.87 | P23:345:WERE:BUFF-345-543:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21817 | 110.2 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21818 | 110.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21818 | 110.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21828 | 109.88 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21828 | 109.88 | P23:345:SUNC:BU_BRK488:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21833 | 109.68 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21833 | 109.73 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21834 | 109.48 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21846 | 110.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21922 | 110.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21922 | 111.12 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21923 | 110.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21924 | 110.28 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21961 | 110.52 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22088 | 114.65 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22096 | 114.7 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22101 | 112.33 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22111 | 115.03 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22111 | 115.03 | Potential P4 Event - POI 531449_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22128 | 111.45 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22128 | 111.45 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2222 | 115.2 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22235 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22235 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22364 | 115.8 | POI 515800_22 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22364 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22589 | 122.24 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2274 | 139.23 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22832 | 121.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22832 | 121.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22847 | 127.99 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22847 | 132.76 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22847 | 135.94 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22847 | 136.42 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22847 | 139.53 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22847 | 140.37 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22847 | 140.41 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22847 | 141.59 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23178 | 117.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23178 | 120.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23178 | 120.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35965 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20199 | 102.67 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20199 | 104.7 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20199 | 104.7 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.347 | 175.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.39526 | 105.96 | P12:115:SPS:T49_1_PRNGLE_BLKHK:::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.39526 | 107.15 | 523214 WRB_REF 115 523396 WRB_SW 115 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.39526 | 110.11 | 523214 WRB_REF 115 523346 BLKHAWK_E 3 115 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41342 | 104.88 | P12:230:SPS:K98::1_CHANN_XIT:: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41357 | 102.85 | P12:345:OKGE:BKRBKR604_2 :::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41362 | 102.34 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41362 | 102.41 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41362 | 102.62 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41362 | 102.63 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41363 | 101.93 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41363 | 101.94 | 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41363 | 102.18 | 539783 CRKCK 3 115 539784 ENSNGW 3 115 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41363 | 102.22 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41363 | 102.25 | P13:115:SUNC:FORTDODGE_GSU:::HV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41363 | 102.64 | P11:24:NPPD:GENTLM2G:2:757:: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41364 | 102.17 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41364 | 102.17 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41364 | 102.23 | P11:345:WERE:JECU2-GEN:::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41364 | 102.23 | P23:345:WERE:JEC-345-20:::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 101.79 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 101.91 | P12:EHV:EES::8PERRYVILLE%:1(1) | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 101.92 | P11:230-22:CLEC::RODEMR 6:1(1) | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 101.93 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 101.93 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 101.93 | P11:EHV:EES::1FRNTR 1!:1(1) | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 101.93 | P11:HV:EES::1CARVLE_C1!:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 101.93 | P12:LV-EHV:EES::7GRIMES%:1FRNTR 1!:1FRNTR 2!:1FRNTR 3!:1FRNTR 4!:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 101.94 | P12:LV-HV:EES::6GYPSY%:1GYP U3!:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.15 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.15 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.15 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.15 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.16 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.16 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.16 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.18 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.19 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.2 | P23:500:EAI-TVA:NBF_WEST M~1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.2 | P23:500:EES-EAI:KEO:B4931 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.21 | P23:345:MEC:LOUISA 964 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.22 | P11:115:XEL:HBR #6 7 8 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.22 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.22 | P23:345:XEL:8P2 KING | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.25 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.25 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.25 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.26 | 531451 MINGO 7 345 531632 SLMNFRK7 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.27 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.28 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.29 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.3 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.48 | 772281 GEN-2023-015 345 772282 G23-015XFMR1 34.5 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.52 | P23:345:XEL:8N8 MNN | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.54 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.54 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.54 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.54 | P23:345:XEL:8N17 SHC | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.54 | P23:345:XEL:8N22 SHC | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.55 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.55 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.56 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.56 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.56 | P23:345:MEC:CBEC 908 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.57 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.57 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.58 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.59 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.59 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.59 | P23:345:MEC:CBEC 905 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.61 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.61 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.62 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.62 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.63 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.78 | 522941 LOBO-T 3 115 522957 POWELL CNR 3 115 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.78 | 772181 GEN-2023-010 230 772182 G23-010XFMR1 34.5 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.78 | 772181 GEN-2023-010 230 772185 G23-010XFMR2 34.5 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.78 | P12:115:GLHP:POWELL-LOBO-DRYTRAILS:::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 102.9 | 522941 LOBO-T 3 115 523099 TC-DRYTRLS 3 115 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 103.15 | GEN-2006-044_POI_523097_Generator_outage | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 103.19 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 103.2 | ASGI-2016-010_POI_523090_Generator_outage | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 103.32 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 103.32 | GEN-2017-100_POI_523090_Generator_outage | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 103.54 | GEN-2023-010_POI_523309_Generator_outage | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 103.58 | GEN-2002-009_POI_523195_Generator_outage | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 103.73 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 103.73 | GEN-2017-047_POI_523120_Generator_outage | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 108.01 | 523344 BLKHAWK_W 3 115 523461 BLACKHAWK1 1 13.8 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 108.58 | 523346 BLKHAWK_E 3 115 523462 BLACKHAWK2 1 13.8 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41366 | 102.27 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41366 | 102.27 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41366 | 102.29 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41366 | 102.35 | P23:500:EES-EAI:KEO:B4921 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41366 | 102.38 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41368 | 102.43 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41369 | 102.41 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41369 | 102.42 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.4137 | 102.45 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41371 | 102.24 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41372 | 102.38 | P23:345:AEPW:PITTSBURG CB 3445A NBTB:::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41372 | 102.38 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT:::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41375 | 102.45 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41375 | 102.56 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41376 | 103.13 | Potential P4 Event - POI 560022_9 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41376 | 103.13 | Potential P4 Event - POI 762216_5 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.4138 | 102.67 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41382 | 102.77 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41384 | 103.41 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41384 | 103.56 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41384 | 103.56 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41386 | 103.09 | Potential P4 Event - POI 762216_14 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41386 | 103.09 | Potential P4 Event - POI 762467_7 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41396 | 103.21 | POI 515800_22 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41396 | 103.24 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41415 | 104.24 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41417 | 104 | 515375 WWRDEHV7 345 516059 BECKHAM7 345 2 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41417 | 104 | P12:345:OKGE:BKRBKR489:::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41441 | 107.6 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41447 | 104.47 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41447 | 105.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41516 | 102.53 | 523977 HARRNG_WST 6 230 523978 HARRNG_MID 6 230 @1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41535 | 108.4 | Potential P4 Event - POI 515375_50 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41538 | 105.28 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41544 | 104.58 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41544 | 104.58 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41605 | 117.31 | Potential P4 Event - POI 523097_33 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41605 | 117.31 | Potential P4 Event - POI 523961_4 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41773 | 106.3 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.44502 | 105.66 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 168 | 193 | 1 | 145.55 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.39526 | 109.01 | P12:115:SPS:T49_1_PRNGLE_BLKHK:::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.39526 | 113.84 | 523214 WRB_REF 115 523346 BLKHAWK_E 3 115 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41342 | 108.42 | P12:230:SPS:K98::1_CHANN_XIT:: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41351 | 105.29 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41357 | 106.28 | P12:345:OKGE:BKRBKR604_2 :::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41362 | 105.74 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41362 | 105.83 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41362 | 106.04 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41362 | 106.04 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41363 | 105.57 | 539783 CRKCK 3 115 539784 ENSNGW 3 115 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41363 | 105.61 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41363 | 105.64 | P13:115:SUNC:FORTDODGE_GSU:::HV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41363 | 106.06 | P11:24:NPPD:GENTLM2G:2:757:: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41364 | 105.31 | 640183 GENTLMN3 345 640500 THEDFRD3 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41364 | 105.57 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41364 | 105.57 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41364 | 105.62 | P11:345:WERE:JECU2-GEN:::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41364 | 105.62 | P23:345:WERE:JEC-345-20:::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.13 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.28 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.29 | P11:EHV:EES::1FRNTR 1!:1(1) | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.3 | P12:LV-HV:EES::6GYPSY%:1GYP U3!:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.31 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.31 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.31 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.31 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.31 | P12:HV:EES::4LEWIS%:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.31 | P12:HV:EES::4LEWIS%:1(1) | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.31 | P12:LV-HV:EES::3GYPSY%:1GYP U2!:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.52 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.52 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.54 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.54 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.54 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.54 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.55 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.55 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.55 | P23:500:EES-EMI:B_WLSN:J2233 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.57 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.58 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.59 | P23:500:EAI-TVA:NBF_WEST M~1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.59 | P23:500:EES-EAI:KEO:B4931 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.61 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.61 | P23:345:MEC:LOUISA 964 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.62 | 531451 MINGO 7 345 531632 SLMNFRK7 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.62 | P11:115:XEL:HBR #6 7 8 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.62 | P23:345:XEL:8P2 KING | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.65 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.65 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.66 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.67 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.67 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.69 | P11:345:WERE:WOLFU1-GEN:::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.69 | P23:345:WERE:WOLF-345-50:::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.89 | 772281 GEN-2023-015 345 772282 G23-015XFMR1 34.5 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.92 | P23:345:XEL:8N8 MNN | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.93 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.93 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.93 | P23:345:XEL:8N17 SHC | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.93 | P23:345:XEL:8N22 SHC | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.94 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.95 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.96 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.96 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.96 | P23:345:MEC:CBEC 908 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.97 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.97 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.98 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.99 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 105.99 | P23:345:MEC:CBEC 905 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106.02 | P11:22:NPPD:COOPER1G:1:983:: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106.02 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106.03 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106.03 | P11:345:MEC-NPPD:COOPER 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106.04 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106.11 | 772181 GEN-2023-010 230 772182 G23-010XFMR1 34.5 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106.11 | 772181 GEN-2023-010 230 772185 G23-010XFMR2 34.5 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106.18 | 522941 LOBO-T 3 115 522957 POWELL CNR 3 115 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106.18 | P12:115:GLHP:POWELL-LOBO-DRYTRAILS:::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106.3 | 522941 LOBO-T 3 115 523099 TC-DRYTRLS 3 115 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106.52 | ASGI-2011-002_POI_523266_Generator_outage | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106.61 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106.61 | ASGI-2016-010_POI_523090_Generator_outage | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106.73 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106.73 | GEN-2017-100_POI_523090_Generator_outage | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 106.87 | GEN-2023-010_POI_523309_Generator_outage | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 107.03 | GEN-2002-009_POI_523195_Generator_outage | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 107.15 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 107.16 | GEN-2017-047_POI_523120_Generator_outage | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 111.28 | 523344 BLKHAWK_W 3 115 523461 BLACKHAWK1 1 13.8 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41365 | 111.84 | 523346 BLKHAWK_E 3 115 523462 BLACKHAWK2 1 13.8 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41366 | 105.52 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41366 | 105.67 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41366 | 105.68 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41366 | 105.68 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41366 | 105.76 | P23:500:EES-EAI:KEO:B4921 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41366 | 105.79 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41368 | 105.86 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41369 | 105.82 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41369 | 105.84 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.4137 | 105.88 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41371 | 105.64 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41372 | 105.79 | P23:345:AEPW:PITTSBURG CB 3445A NBTB:::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41372 | 105.79 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT:::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41375 | 105.87 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41375 | 105.99 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41376 | 106.6 | Potential P4 Event - POI 560022_9 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41376 | 106.6 | Potential P4 Event - POI 762216_5 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.4138 | 106.12 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41382 | 106.23 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41384 | 106.93 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41384 | 107.1 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41384 | 107.1 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41386 | 106.57 | Potential P4 Event - POI 762216_14 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41386 | 106.57 | Potential P4 Event - POI 762467_7 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41396 | 106.73 | POI 515800_22 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41396 | 106.78 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41415 | 107.79 | P42:345:OKGE:SB_BOER7384:::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41417 | 107.54 | 515375 WWRDEHV7 345 516059 BECKHAM7 345 2 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41417 | 107.54 | P12:345:OKGE:BKRBKR489:::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41441 | 110.65 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41441 | 111.36 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41447 | 108.12 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41447 | 109.03 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41516 | 105.96 | 523977 HARRNG_WST 6 230 523978 HARRNG_MID 6 230 @1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41535 | 112.38 | Potential P4 Event - POI 515375_50 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41538 | 108.97 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41544 | 108.19 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41544 | 108.2 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41605 | 121.81 | Potential P4 Event - POI 523097_33 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41605 | 121.81 | Potential P4 Event - POI 523961_4 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.41773 | 109.93 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 0.44502 | 109.13 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 168 | 193 | 1 | 143.52 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21418 | 183.79 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2152 | 179.87 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2152 | 179.92 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2152 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2152 | 191.94 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21969 | 184.51 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21396 | 184.16 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21498 | 180.34 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21498 | 180.35 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21498 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21498 | 192.34 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21947 | 184.91 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20014 | 165.4 | Potential P4 Event - POI 527656_0 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.2073 | 114.05 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.2073 | 114.9 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20217 | 136.58 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 126.41 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 130.57 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 133.59 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 134.05 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 136.94 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 137.75 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 137.78 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 138.96 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 116.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 119.14 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 119.15 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2936 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28327 | 175.43 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2206 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22083 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2236 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22378 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22589 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.226 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22616 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22621 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22622 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22626 | 101.44 | Potential P4 Event - POI 523823_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22771 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22855 | 104.75 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22861 | 104.09 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22861 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23058 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24019 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24771 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26243 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37835 | 152.61 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41566 | 184.51 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41702 | 183.79 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 179.87 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 179.92 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 191.94 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22037 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24078 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37802 | 153.1 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41526 | 184.91 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4166 | 184.16 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 180.34 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 180.35 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 192.34 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20217 | 139.23 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 127.99 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 132.76 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 135.94 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 136.42 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 139.53 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 140.37 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 140.41 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 141.59 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 117.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 120.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 120.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2936 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28327 | 175.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20014 | 165.4 | Potential P4 Event - POI 527656_0 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.2073 | 114.05 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.2073 | 114.9 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20217 | 136.58 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 126.41 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 130.57 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 133.59 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 134.05 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 136.94 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 137.75 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 137.78 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 138.96 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 116.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 119.14 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 119.15 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2936 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28327 | 175.43 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2206 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22083 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2236 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22378 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22589 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.226 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22616 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22621 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22622 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22626 | 101.44 | Potential P4 Event - POI 523823_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22771 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22855 | 104.75 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22861 | 104.09 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22861 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23058 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24019 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24771 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26243 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37835 | 152.61 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41566 | 184.51 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41702 | 183.79 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 179.87 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 179.92 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 191.94 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22037 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24078 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37802 | 153.1 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41526 | 184.91 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4166 | 184.16 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 180.34 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 180.35 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 192.34 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20217 | 139.23 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 127.99 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 132.76 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 135.94 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 136.42 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 139.53 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 140.37 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 140.41 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 141.59 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 117.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 120.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 120.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2936 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28327 | 175.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21984 | 162.73 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21984 | 164.74 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21984 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21999 | 165.01 | Potential P4 Event - POI 527656_13 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21999 | 165.01 | Potential P4 Event - POI 527656_14 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22027 | 165.4 | Potential P4 Event - POI 527656_0 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21929 | 114.05 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21929 | 114.9 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20463 | 116.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20463 | 119.14 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20463 | 119.15 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.27695 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.26721 | 175.43 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22309 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22572 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22582 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22608 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22834 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22844 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2286 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22865 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22866 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22871 | 101.44 | Potential P4 Event - POI 523823_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23002 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23098 | 104.75 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23104 | 104.09 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23104 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23303 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24294 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25177 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.27211 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37207 | 152.61 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4202 | 184.51 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42171 | 183.79 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42542 | 179.87 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42542 | 179.92 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42542 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42542 | 191.94 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22289 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24966 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37174 | 153.1 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41979 | 184.91 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42128 | 184.16 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42498 | 180.34 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42498 | 180.35 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42498 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42498 | 192.34 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20463 | 117.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20463 | 120.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20463 | 120.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.27695 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.26721 | 175.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21984 | 162.73 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21984 | 164.74 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21984 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21999 | 165.01 | Potential P4 Event - POI 527656_13 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21999 | 165.01 | Potential P4 Event - POI 527656_14 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22027 | 165.4 | Potential P4 Event - POI 527656_0 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21929 | 114.05 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21929 | 114.9 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20463 | 116.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20463 | 119.14 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20463 | 119.15 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.27695 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.26721 | 175.43 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22309 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22572 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22582 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22608 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22834 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22844 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2286 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22865 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22866 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22871 | 101.44 | Potential P4 Event - POI 523823_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23002 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23098 | 104.75 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23104 | 104.09 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23104 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23303 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24294 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25177 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.27211 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37207 | 152.61 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4202 | 184.51 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42171 | 183.79 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42542 | 179.87 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42542 | 179.92 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42542 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42542 | 191.94 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22289 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24966 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37174 | 153.1 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41979 | 184.91 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42128 | 184.16 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42498 | 180.34 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42498 | 180.35 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42498 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42498 | 192.34 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20463 | 117.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20463 | 120.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20463 | 120.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.27695 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.26721 | 175.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20014 | 165.4 | Potential P4 Event - POI 527656_0 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.2073 | 114.05 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.2073 | 114.9 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20217 | 136.58 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 126.41 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 130.57 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 133.59 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 134.05 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 136.94 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 137.75 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 137.78 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 138.96 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 116.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 119.14 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 119.15 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2936 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28327 | 175.43 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2206 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22083 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2236 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22378 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22589 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.226 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22616 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22621 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22622 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22626 | 101.44 | Potential P4 Event - POI 523823_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22771 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22855 | 104.75 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22861 | 104.09 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22861 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23058 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24019 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24771 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26243 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37835 | 152.61 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41566 | 184.51 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41702 | 183.79 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 179.87 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 179.92 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 191.94 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22037 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24078 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37802 | 153.1 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41526 | 184.91 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4166 | 184.16 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 180.34 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 180.35 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 192.34 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20217 | 139.23 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 127.99 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 132.76 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 135.94 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 136.42 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 139.53 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 140.37 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 140.41 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 141.59 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 117.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 120.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 120.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2936 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28327 | 175.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.2112 | 162.73 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.2112 | 164.74 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.2112 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21133 | 165.01 | Potential P4 Event - POI 527656_13 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21133 | 165.01 | Potential P4 Event - POI 527656_14 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21166 | 165.4 | Potential P4 Event - POI 527656_0 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.20333 | 114.05 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.20333 | 114.9 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20137 | 116.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20137 | 119.14 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20137 | 119.15 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.27607 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.26635 | 175.43 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21283 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21543 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21836 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21844 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22075 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22085 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22101 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22106 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22108 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22112 | 101.44 | Potential P4 Event - POI 523823_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22262 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22342 | 104.75 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22348 | 104.09 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22348 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22564 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23592 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24202 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2644 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.36385 | 152.61 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.40634 | 184.51 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4073 | 183.79 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41082 | 179.87 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41082 | 179.92 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41082 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41082 | 191.94 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21646 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24258 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.36353 | 153.1 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.40594 | 184.91 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.40688 | 184.16 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4104 | 180.34 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4104 | 180.35 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4104 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4104 | 192.34 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20137 | 117.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20137 | 120.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20137 | 120.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.27607 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.26635 | 175.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2419 | 152.61 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26204 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.30809 | 183.79 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31026 | 179.87 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31026 | 179.92 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31026 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31026 | 191.94 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31112 | 184.51 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24042 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24169 | 153.1 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.30778 | 184.16 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.30994 | 180.34 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.30994 | 180.35 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.30994 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.30994 | 192.34 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31082 | 184.91 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22637 | 162.73 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22637 | 164.74 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22637 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.2265 | 165.01 | Potential P4 Event - POI 527656_13 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.2265 | 165.01 | Potential P4 Event - POI 527656_14 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22679 | 165.4 | Potential P4 Event - POI 527656_0 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.22519 | 114.05 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.22519 | 114.9 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20914 | 116.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20914 | 119.14 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20914 | 119.15 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.28277 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.27282 | 175.43 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2165 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21817 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22106 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22117 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22347 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22357 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22373 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22378 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22379 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22383 | 101.44 | Potential P4 Event - POI 523823_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22527 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22613 | 104.75 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22618 | 104.09 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22618 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22828 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23839 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24762 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26647 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37017 | 152.61 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4113 | 184.51 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41245 | 183.79 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41604 | 179.87 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41604 | 179.92 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41604 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41604 | 191.94 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21872 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24448 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.36984 | 153.1 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41089 | 184.91 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41203 | 184.16 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41561 | 180.34 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41561 | 180.35 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41561 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41561 | 192.34 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20914 | 117.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20914 | 120.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20914 | 120.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.28277 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.27282 | 175.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20942 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26671 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26814 | 152.61 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34826 | 183.79 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34972 | 184.51 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.35098 | 179.87 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.35098 | 179.92 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.35098 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.35098 | 191.94 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2447 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.26791 | 153.1 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.34791 | 184.16 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.34937 | 184.91 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.35061 | 180.34 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.35061 | 180.35 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.35061 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.35061 | 192.34 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21306 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21655 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21845 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21953 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21956 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22181 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22191 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22207 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22212 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22213 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22218 | 101.44 | Potential P4 Event - POI 523823_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22345 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22446 | 104.75 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22451 | 104.09 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22451 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22684 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23818 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28574 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31158 | 152.61 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.40846 | 184.51 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4094 | 183.79 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41294 | 179.87 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41294 | 179.92 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41294 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41294 | 191.94 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21852 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.26216 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31131 | 153.1 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.40806 | 184.91 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.40898 | 184.16 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41252 | 180.34 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41252 | 180.35 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41252 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41252 | 192.34 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21545 | 152.61 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23879 | 183.79 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24008 | 179.87 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24008 | 179.92 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24008 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24008 | 191.94 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24385 | 184.51 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21526 | 153.1 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23855 | 184.16 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23983 | 180.34 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23983 | 180.35 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23983 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23983 | 192.34 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24361 | 184.91 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23403 | 152.61 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25697 | 183.79 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2585 | 179.87 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2585 | 179.92 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2585 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2585 | 191.94 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26138 | 184.51 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23382 | 153.1 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25671 | 184.16 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25823 | 180.34 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25823 | 180.35 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25823 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25823 | 192.34 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.26113 | 184.91 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20006 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20011 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20013 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20017 | 101.44 | Potential P4 Event - POI 523823_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20184 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20252 | 104.75 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20258 | 104.09 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20258 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2055 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21859 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.27414 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.27702 | 152.61 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28766 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.36766 | 183.79 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.36836 | 184.51 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37064 | 179.87 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37064 | 179.92 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37064 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37064 | 191.94 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.20056 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25152 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.27677 | 153.1 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.36729 | 184.16 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.368 | 184.91 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37026 | 180.34 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37026 | 180.35 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37026 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37026 | 192.34 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20808 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24231 | 159.35 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26067 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.30918 | 187.51 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31141 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31141 | 188.56 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31141 | 188.56 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31141 | 196.01 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31197 | 188.69 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23916 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2421 | 160.18 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.30887 | 188.08 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31109 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31109 | 189.17 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31109 | 189.17 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31109 | 196.69 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31166 | 189.3 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20059 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20059 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.09 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.1 | P11:21:EES:RVB:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.12 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.18 | P11:25:EES:WATERF:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.18 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.18 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20252 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20264 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20268 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20268 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20269 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20293 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20294 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20294 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20296 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20301 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20344 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20344 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20409 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2047 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20512 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20513 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2065 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20662 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20688 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20691 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20694 | 103.51 | Potential P4 Event - POI 523823_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20855 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20925 | 106.63 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20932 | 106.08 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20932 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21183 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22269 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22442 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.27642 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.29213 | 159.35 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38025 | 187.51 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38025 | 188.69 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38344 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38344 | 188.56 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38344 | 188.56 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38344 | 196.01 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2059 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25361 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.29187 | 160.18 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37986 | 188.08 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37988 | 189.3 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38304 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38304 | 189.17 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38304 | 189.17 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38304 | 196.69 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 528413 TAYLOR 3 115 528449 W_BENDER 3 115 1 | 159 | 165 | 1 | 133.01 | 528355 MADDOX 3 115 762442 G18-004-TAP 115 1 | TDF Impact | Rebuild the existing TAYLOR3 to W_BENDER3 115 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.20345 | 103.2 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.20608 | 121.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525549 TOLK 7 345 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.20345 | 103.84 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.20608 | 122.42 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20093 | 151.79 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 145.67 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 147.96 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 148.9 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 151.28 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 134.4 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 136.62 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 136.62 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29198 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.2817 | 203.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.09 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.1 | P11:21:EES:RVB:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.12 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.18 | P11:25:EES:WATERF:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.18 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.18 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21945 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22059 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22071 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22076 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22077 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22077 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22096 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22101 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22102 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22102 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22158 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22158 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22215 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22228 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22267 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22268 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22274 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22279 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22279 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22389 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22452 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22464 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22489 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22493 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22496 | 103.51 | Potential P4 Event - POI 523823_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22648 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22723 | 106.63 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2273 | 106.08 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2273 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22908 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23886 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24614 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24614 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24614 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26059 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37603 | 159.35 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41286 | 188.69 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4143 | 187.51 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 188.56 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 188.56 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 196.01 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21915 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23909 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.3757 | 160.18 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41245 | 189.3 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41387 | 188.08 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 189.17 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 189.17 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 196.69 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20093 | 155.33 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 148.52 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 151.14 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.15 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 154.71 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.72 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.73 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.73 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 136.37 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 138.58 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 138.58 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29198 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.2817 | 203.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.28037 | 129.93 | GEN-2023-237_POI_560022_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3489 | 151.79 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.34961 | 130.43 | Potential P4 Event - POI 560022_14 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35054 | 145.67 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35054 | 147.96 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35054 | 148.9 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35054 | 151.28 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35054 | 152.22 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35054 | 152.22 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35054 | 152.22 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35054 | 152.22 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3555 | 125.77 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3555 | 125.77 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35564 | 125.15 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35572 | 125.36 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35572 | 125.53 | P23:500:EES-EAI:DELL:B8320::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35573 | 125.34 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.13 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.18 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.34 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.34 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.34 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.35 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.37 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.38 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.4 | P23:500:EES:MOUNTSOLIVE:R3976::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.44 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.44 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.5 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.51 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.54 | P13:138:EES:LC:T1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.54 | P13:138:EES:LC:T2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.59 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.61 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.61 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.61 | P11:EHV:EES::1FRNTR 1!:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.63 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.66 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.66 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.7 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.71 | P13:230,22:CLEC::G2RODEMR::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.75 | P11:18:EES:NINEMI:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.82 | P13:230:EES:NINEMI:AT4 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.85 | P11:EHV:EES::1TRACTBEL C1:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.85 | P13:230,22:CLEC::G3MADISN::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.86 | P11:26:EES-EAI:INDEP2:1:D401 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.86 | P11:EHV:EES::1ISES U2:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.87 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.87 | P13:230:EES:NINEMI:AT5 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.88 | P11:26:EES:NINEMI:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.88 | P11:HV:EES::1NMIL U5!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.89 | P11:22:CLEC:RODEMR1:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.92 | P12:EHV:EES::8WHT BLUFF%:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.92 | P13:500:EES-EAI:WH_BLF:ST2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.93 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.96 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126 | P13:345,24:CLEC::G1DOLHILL::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.06 | P12:EHV:EES::8ANO%:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.09 | P11:22:EES-EAI:ARK_NU:1:D395 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.18 | P11:21:EES:RVB:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.18 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.18 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.18 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.18 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.2 | P11:HV:EES::1LEWIS_U3 ST:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.21 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.21 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.26 | P11:25:EES:WATERF:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.26 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.27 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.46 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.46 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.46 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.51 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.51 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.55 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 127.28 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 127.75 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 129.87 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 129.92 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35575 | 125.34 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35575 | 125.34 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35575 | 125.35 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35575 | 125.35 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35579 | 125.39 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35579 | 125.39 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3558 | 125.51 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3558 | 125.51 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35581 | 125.5 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35583 | 125.55 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35583 | 125.55 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35584 | 124.96 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35589 | 125.45 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3559 | 125.65 | P23:345:WERE:WICH-345-50:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35592 | 125.83 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35598 | 125.65 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35602 | 127.51 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35613 | 125.74 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35614 | 126.01 | P23:345:WERE:BUFF-345-534:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35614 | 126.01 | P23:345:WERE:BUFF-345-543:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3562 | 125.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35643 | 127.73 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35644 | 126.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35651 | 127.27 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35655 | 127.45 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35664 | 127.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35669 | 127.94 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3567 | 127.95 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35673 | 126.64 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35673 | 126.64 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35683 | 129.27 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35691 | 126.29 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35691 | 126.34 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35718 | 127.45 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35726 | 127.87 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35726 | 127.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35761 | 127.7 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35794 | 127.77 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3584 | 132.96 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35879 | 129.85 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35889 | 129.79 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35905 | 129.97 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35962 | 133.28 | POI 515800_22 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35962 | 133.4 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36044 | 132.53 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36117 | 137.84 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36117 | 138.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36596 | 134.4 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36596 | 136.62 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36596 | 136.62 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36612 | 138.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.58908 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.24433 | 113.23 | GEN-2023-237_POI_560022_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30405 | 132.28 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30467 | 113.67 | Potential P4 Event - POI 560022_14 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30548 | 126.95 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30548 | 128.95 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30548 | 129.77 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30548 | 131.84 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30548 | 132.66 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30548 | 132.66 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30548 | 132.66 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30548 | 132.66 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3098 | 109.61 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3098 | 109.61 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30993 | 109.07 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31 | 109.25 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31 | 109.4 | P23:500:EES-EAI:DELL:B8320::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.04 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.05 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.06 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.25 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.26 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.27 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.29 | P23:500:EES:MOUNTSOLIVE:R3976::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.32 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.32 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.37 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.39 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.41 | P13:138:EES:LC:T1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.41 | P13:138:EES:LC:T2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.46 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.47 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.47 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.47 | P11:EHV:EES::1FRNTR 1!:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.49 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.51 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.51 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.55 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.56 | P13:230,22:CLEC::G2RODEMR::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.6 | P11:18:EES:NINEMI:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.66 | P13:230:EES:NINEMI:AT4 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.68 | P11:EHV:EES::1TRACTBEL C1:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.68 | P13:230,22:CLEC::G3MADISN::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.69 | P11:26:EES-EAI:INDEP2:1:D401 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.69 | P11:EHV:EES::1ISES U2:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.7 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.7 | P13:230:EES:NINEMI:AT5 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.71 | P11:22:CLEC:RODEMR1:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.71 | P11:26:EES:NINEMI:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.71 | P11:HV:EES::1NMIL U5!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.74 | P12:EHV:EES::8WHT BLUFF%:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.74 | P13:500:EES-EAI:WH_BLF:ST2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.75 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.75 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.77 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.81 | P13:345,24:CLEC::G1DOLHILL::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.86 | P12:EHV:EES::8ANO%:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.89 | P11:22:EES-EAI:ARK_NU:1:D395 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.96 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.96 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.97 | P11:21:EES:RVB:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.97 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.97 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.99 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.99 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.99 | P11:HV:EES::1LEWIS_U3 ST:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.04 | P11:25:EES:WATERF:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.04 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.04 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.21 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.21 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.21 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.26 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.26 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.29 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.92 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 111.34 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 113.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 113.23 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31002 | 109.24 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31002 | 109.25 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31006 | 109.28 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31006 | 109.28 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31006 | 109.39 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31006 | 109.39 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31008 | 109.38 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31009 | 109.41 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31009 | 109.42 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3101 | 108.91 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3101 | 108.91 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31014 | 109.33 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31015 | 109.5 | P23:345:WERE:WICH-345-50:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31017 | 109.66 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31022 | 109.51 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31026 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31036 | 109.58 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31036 | 109.81 | P23:345:WERE:BUFF-345-534:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31036 | 109.81 | P23:345:WERE:BUFF-345-543:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31042 | 109.38 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31062 | 110.47 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31062 | 111.32 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31069 | 110.92 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31072 | 111.07 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3108 | 110.76 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31085 | 111.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31085 | 111.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31088 | 110.37 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31088 | 110.37 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31096 | 112.66 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31103 | 110.06 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31103 | 110.11 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31127 | 111.08 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31134 | 111.44 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31134 | 111.44 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31165 | 111.29 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31193 | 111.35 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31233 | 115.88 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31267 | 113.16 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31276 | 113.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3129 | 113.27 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3134 | 116.16 | POI 515800_22 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3134 | 116.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31411 | 115.5 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31474 | 120.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31474 | 120.94 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31892 | 117.13 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31892 | 119.07 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31892 | 119.07 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31906 | 120.95 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.56835 | 203.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23006 | 103.24 | GEN-2023-237_POI_560022_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.09 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.1 | P11:21:EES:RVB:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.12 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.18 | P11:25:EES:WATERF:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.18 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.18 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33858 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33862 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.3387 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33875 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33884 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33884 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33888 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33891 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33902 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33902 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33902 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33902 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33926 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33926 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33942 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33942 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34033 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.3408 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34134 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34152 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34192 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34206 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.3423 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34235 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34237 | 103.51 | Potential P4 Event - POI 523823_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34324 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34408 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34423 | 106.63 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34429 | 106.08 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34429 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34545 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34545 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34545 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34573 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.35961 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.62715 | 188.69 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.63714 | 187.51 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.6438 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.6438 | 188.56 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.6438 | 188.56 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.6438 | 196.01 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.65295 | 159.35 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.3172 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.32994 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.62654 | 189.3 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.63649 | 188.08 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.64314 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.64314 | 189.17 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.64314 | 189.17 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.64314 | 196.69 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.65237 | 160.18 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.28037 | 131.12 | GEN-2023-237_POI_560022_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3489 | 155.33 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.34961 | 131.58 | Potential P4 Event - POI 560022_14 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35054 | 148.52 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35054 | 151.14 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35054 | 152.15 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35054 | 154.71 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35054 | 155.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35054 | 155.72 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35054 | 155.73 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35054 | 155.73 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3555 | 126.52 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3555 | 126.52 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35564 | 125.9 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35572 | 126.11 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35572 | 126.28 | P23:500:EES-EAI:DELL:B8320::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35573 | 126.09 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.89 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.93 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.94 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.09 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.09 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.1 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.1 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.12 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.13 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.15 | P23:500:EES:MOUNTSOLIVE:R3976::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.21 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.21 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.25 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.26 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.29 | P13:138:EES:LC:T1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.29 | P13:138:EES:LC:T2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.34 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.35 | P11:EHV:EES::1FRNTR 1!:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.36 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.36 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.38 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.4 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.4 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.45 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.46 | P13:230,22:CLEC::G2RODEMR::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.5 | P11:18:EES:NINEMI:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.57 | P13:230:EES:NINEMI:AT4 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.6 | P11:EHV:EES::1TRACTBEL C1:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.6 | P13:230,22:CLEC::G3MADISN::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.61 | P11:26:EES-EAI:INDEP2:1:D401 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.61 | P11:EHV:EES::1ISES U2:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.62 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.62 | P13:230:EES:NINEMI:AT5 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.63 | P11:26:EES:NINEMI:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.63 | P11:HV:EES::1NMIL U5!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.64 | P11:22:CLEC:RODEMR1:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.67 | P12:EHV:EES::8WHT BLUFF%:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.67 | P13:500:EES-EAI:WH_BLF:ST2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.68 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.68 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.7 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.74 | P13:345,24:CLEC::G1DOLHILL::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.81 | P12:EHV:EES::8ANO%:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.84 | P11:22:EES-EAI:ARK_NU:1:D395 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.92 | P11:21:EES:RVB:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.92 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.92 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.94 | P11:HV:EES::1LEWIS_U3 ST:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.96 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.96 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 127.01 | P11:25:EES:WATERF:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 127.01 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 127.01 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 127.33 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 127.33 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 127.33 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 127.39 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 127.39 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 127.45 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 128 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 128.77 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 130.63 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 131.12 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35575 | 126.09 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35575 | 126.1 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35575 | 126.1 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35579 | 126.14 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35579 | 126.14 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3558 | 126.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3558 | 126.26 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35581 | 126.25 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35583 | 126.29 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35583 | 126.3 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35584 | 125.72 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35589 | 126.2 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3559 | 126.39 | P23:345:WERE:WICH-345-50:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35592 | 126.58 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35598 | 126.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35602 | 128.58 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35613 | 126.49 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35614 | 126.75 | P23:345:WERE:BUFF-345-534:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35614 | 126.75 | P23:345:WERE:BUFF-345-543:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3562 | 126.26 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35643 | 128.46 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35651 | 128 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35655 | 128.18 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35664 | 127.78 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35669 | 128.71 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3567 | 128.72 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35673 | 127.38 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35673 | 127.38 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35683 | 130.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35686 | 127.5 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35691 | 127.03 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35691 | 127.08 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35718 | 128.3 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35726 | 128.69 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35726 | 128.69 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35761 | 128.37 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35794 | 128.45 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3584 | 133.73 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35879 | 130.56 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35889 | 130.51 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35905 | 130.68 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35962 | 133.73 | POI 515800_22 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35962 | 133.85 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36044 | 133.15 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36117 | 138.8 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36117 | 139.72 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36596 | 136.37 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36596 | 138.58 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36596 | 138.58 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36612 | 139.88 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.58908 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.24433 | 114.27 | GEN-2023-237_POI_560022_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30405 | 135.37 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30467 | 114.68 | Potential P4 Event - POI 560022_14 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30548 | 129.44 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30548 | 131.72 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30548 | 132.6 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30548 | 134.83 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30548 | 135.72 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30548 | 135.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30548 | 135.72 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30548 | 135.72 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3098 | 110.27 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3098 | 110.27 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30993 | 109.72 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31 | 109.91 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31 | 110.05 | P23:500:EES-EAI:DELL:B8320::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.69 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.71 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.72 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.9 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.92 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.92 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.94 | P23:500:EES:MOUNTSOLIVE:R3976::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.99 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.99 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.03 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.04 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.06 | P13:138:EES:LC:T1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.06 | P13:138:EES:LC:T2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.11 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.12 | P11:EHV:EES::1FRNTR 1!:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.13 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.13 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.15 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.16 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.16 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.2 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.21 | P13:230,22:CLEC::G2RODEMR::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.25 | P11:18:EES:NINEMI:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.31 | P13:230:EES:NINEMI:AT4 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.33 | P13:230,22:CLEC::G3MADISN::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.34 | P11:26:EES-EAI:INDEP2:1:D401 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.34 | P11:EHV:EES::1ISES U2:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.34 | P11:EHV:EES::1TRACTBEL C1:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.35 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.35 | P13:230:EES:NINEMI:AT5 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.36 | P11:26:EES:NINEMI:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.36 | P11:HV:EES::1NMIL U5!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.37 | P11:22:CLEC:RODEMR1:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.4 | P12:EHV:EES::8WHT BLUFF%:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.4 | P13:500:EES-EAI:WH_BLF:ST2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.41 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.41 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.43 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.46 | P13:345,24:CLEC::G1DOLHILL::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.52 | P12:EHV:EES::8ANO%:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.55 | P11:22:EES-EAI:ARK_NU:1:D395 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.62 | P11:21:EES:RVB:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.62 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.62 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.62 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.62 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.64 | P11:HV:EES::1LEWIS_U3 ST:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.65 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.65 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.69 | P11:25:EES:WATERF:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.69 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.69 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.97 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.97 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.97 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 111.02 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 111.02 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 111.08 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 111.55 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 112.23 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 113.85 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 114.27 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31002 | 109.9 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31002 | 109.9 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31006 | 109.93 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31006 | 109.94 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31006 | 110.04 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31006 | 110.04 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31008 | 110.03 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31009 | 110.07 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31009 | 110.07 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3101 | 109.57 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3101 | 109.57 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31014 | 109.98 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31015 | 110.15 | P23:345:WERE:WICH-345-50:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31017 | 110.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31022 | 110.06 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31026 | 112.06 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31036 | 110.24 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31036 | 110.47 | P23:345:WERE:BUFF-345-534:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31036 | 110.47 | P23:345:WERE:BUFF-345-543:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31042 | 110.04 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31062 | 111.95 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31069 | 111.56 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31072 | 111.71 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3108 | 111.37 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31085 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31085 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31088 | 111.01 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31088 | 111.01 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31096 | 113.37 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31099 | 111.12 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31103 | 110.71 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31103 | 110.75 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31127 | 111.82 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31134 | 112.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31134 | 112.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31165 | 111.88 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31193 | 111.95 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31233 | 116.55 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31267 | 113.79 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31276 | 113.74 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3129 | 113.89 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3134 | 116.55 | POI 515800_22 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3134 | 116.65 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31411 | 116.04 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31474 | 120.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31474 | 121.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31892 | 118.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31892 | 120.77 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31892 | 120.78 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31906 | 121.91 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.56835 | 203.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.20345 | 103.2 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.20608 | 121.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525549 TOLK 7 345 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.20345 | 103.84 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.20608 | 122.42 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20093 | 151.79 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 145.67 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 147.96 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 148.9 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 151.28 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 134.4 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 136.62 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 136.62 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29198 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.2817 | 203.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.09 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.1 | P11:21:EES:RVB:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.12 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.18 | P11:25:EES:WATERF:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.18 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.18 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21945 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22059 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22071 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22076 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22077 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22077 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22096 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22101 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22102 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22102 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22158 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22158 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22215 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22228 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22267 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22268 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22274 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22279 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22279 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22389 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22452 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22464 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22489 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22493 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22496 | 103.51 | Potential P4 Event - POI 523823_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22648 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22723 | 106.63 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2273 | 106.08 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2273 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22908 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23886 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24614 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24614 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24614 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26059 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37603 | 159.35 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41286 | 188.69 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4143 | 187.51 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 188.56 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 188.56 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 196.01 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21915 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23909 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.3757 | 160.18 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41245 | 189.3 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41387 | 188.08 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 189.17 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 189.17 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 196.69 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20093 | 155.33 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 148.52 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 151.14 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.15 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 154.71 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.72 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.73 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.73 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 136.37 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 138.58 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 138.58 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29198 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.2817 | 203.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25641 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25664 | 159.35 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.32604 | 187.51 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.32816 | 188.69 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.3285 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.3285 | 188.56 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.3285 | 188.56 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.3285 | 196.01 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23526 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25642 | 160.18 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.3257 | 188.08 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.32784 | 189.3 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.32816 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.32816 | 189.17 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.32816 | 189.17 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.32816 | 196.69 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2033 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25764 | 159.35 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28123 | 187.51 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28313 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28313 | 188.56 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28313 | 188.56 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28313 | 196.01 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28466 | 188.69 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25742 | 160.18 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.28094 | 188.08 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.28283 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.28283 | 189.17 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.28283 | 189.17 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.28283 | 196.69 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.28438 | 189.3 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2033 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21383 | 130.43 | Potential P4 Event - POI 560022_14 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21597 | 125.77 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21597 | 125.77 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21612 | 125.15 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21619 | 125.53 | P23:500:EES-EAI:DELL:B8320::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2162 | 125.34 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2162 | 125.36 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.13 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.18 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.34 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.34 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.34 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.35 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.37 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.38 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.4 | P23:500:EES:MOUNTSOLIVE:R3976::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.44 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.44 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.5 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.51 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.54 | P13:138:EES:LC:T1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.54 | P13:138:EES:LC:T2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.59 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.61 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.61 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.61 | P11:EHV:EES::1FRNTR 1!:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.63 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.66 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.66 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.7 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.71 | P13:230,22:CLEC::G2RODEMR::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.75 | P11:18:EES:NINEMI:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.82 | P13:230:EES:NINEMI:AT4 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.85 | P11:EHV:EES::1TRACTBEL C1:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.85 | P13:230,22:CLEC::G3MADISN::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.86 | P11:26:EES-EAI:INDEP2:1:D401 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.86 | P11:EHV:EES::1ISES U2:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.87 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.87 | P13:230:EES:NINEMI:AT5 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.88 | P11:26:EES:NINEMI:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.88 | P11:HV:EES::1NMIL U5!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.89 | P11:22:CLEC:RODEMR1:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.92 | P12:EHV:EES::8WHT BLUFF%:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.92 | P13:500:EES-EAI:WH_BLF:ST2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.93 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.96 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126 | P13:345,24:CLEC::G1DOLHILL::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.06 | P12:EHV:EES::8ANO%:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.09 | P11:22:EES-EAI:ARK_NU:1:D395 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.18 | P11:21:EES:RVB:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.18 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.18 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.18 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.18 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.2 | P11:HV:EES::1LEWIS_U3 ST:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.21 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.21 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.26 | P11:25:EES:WATERF:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.26 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.27 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.46 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.46 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.46 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.51 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.51 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.55 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 127.28 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 127.75 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 129.87 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 129.92 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21622 | 125.35 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21622 | 125.35 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21623 | 125.34 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21623 | 125.34 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21627 | 125.39 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21627 | 125.39 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 125.5 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 125.51 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 125.51 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21631 | 124.96 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21631 | 125.55 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21631 | 125.55 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2164 | 125.45 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21641 | 125.65 | P23:345:WERE:WICH-345-50:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21647 | 125.65 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21661 | 125.83 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21663 | 125.74 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21669 | 126.01 | P23:345:WERE:BUFF-345-534:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21669 | 126.01 | P23:345:WERE:BUFF-345-543:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21672 | 125.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2172 | 127.73 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21728 | 127.27 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21732 | 127.45 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21733 | 126.64 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21733 | 126.64 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21736 | 126.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2175 | 127.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21751 | 126.29 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21751 | 126.34 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21823 | 127.51 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21823 | 127.7 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21827 | 127.94 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21827 | 127.95 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21863 | 127.77 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21995 | 129.85 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21998 | 129.27 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22004 | 129.79 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22021 | 129.97 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22041 | 127.87 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22041 | 127.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22137 | 132.96 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22148 | 127.45 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22188 | 132.53 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22262 | 133.28 | POI 515800_22 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22262 | 133.4 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22472 | 138.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22618 | 151.79 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22724 | 145.67 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22724 | 147.96 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22724 | 148.9 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22724 | 151.28 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22724 | 152.22 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22724 | 152.22 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22724 | 152.22 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22724 | 152.22 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22741 | 137.84 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22741 | 138.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23061 | 134.4 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23061 | 136.62 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23061 | 136.62 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35803 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20097 | 117.13 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20097 | 119.07 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20097 | 119.07 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.34543 | 203.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.09 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.1 | P11:21:EES:RVB:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.12 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.18 | P11:25:EES:WATERF:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.18 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.18 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23134 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23236 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23274 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23285 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2329 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23292 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23292 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23301 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23316 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23317 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23317 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23356 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23428 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23438 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23439 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23485 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23583 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23587 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23587 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23634 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23634 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23663 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23675 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23701 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23704 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23707 | 103.51 | Potential P4 Event - POI 523823_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23857 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23932 | 106.63 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23939 | 106.08 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23939 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24064 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24239 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24239 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24239 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24809 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24937 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42328 | 159.35 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.43473 | 188.69 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.43717 | 187.51 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.44116 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.44116 | 188.56 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.44116 | 188.56 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.44116 | 196.01 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22762 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2288 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42291 | 160.18 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.43431 | 189.3 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.43673 | 188.08 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4407 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4407 | 189.17 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4407 | 189.17 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4407 | 196.69 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21383 | 131.58 | Potential P4 Event - POI 560022_14 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21597 | 126.52 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21597 | 126.52 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21612 | 125.9 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21619 | 126.28 | P23:500:EES-EAI:DELL:B8320::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2162 | 126.09 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2162 | 126.11 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.89 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.93 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 125.94 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.09 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.09 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.1 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.1 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.12 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.13 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.15 | P23:500:EES:MOUNTSOLIVE:R3976::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.21 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.21 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.25 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.26 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.29 | P13:138:EES:LC:T1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.29 | P13:138:EES:LC:T2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.34 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.35 | P11:EHV:EES::1FRNTR 1!:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.36 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.36 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.38 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.4 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.4 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.45 | P23:500:EES:SANS SOUCI:B3925::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.46 | P13:230,22:CLEC::G2RODEMR::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.5 | P11:18:EES:NINEMI:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.57 | P13:230:EES:NINEMI:AT4 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.6 | P11:EHV:EES::1TRACTBEL C1:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.6 | P13:230,22:CLEC::G3MADISN::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.61 | P11:26:EES-EAI:INDEP2:1:D401 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.61 | P11:EHV:EES::1ISES U2:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.62 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.62 | P13:230:EES:NINEMI:AT5 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.63 | P11:26:EES:NINEMI:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.63 | P11:HV:EES::1NMIL U5!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.64 | P11:22:CLEC:RODEMR1:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.67 | P12:EHV:EES::8WHT BLUFF%:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.67 | P13:500:EES-EAI:WH_BLF:ST2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.68 | P11:26:EES-EAI:WH_BLF:1:D388 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.68 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.7 | P11:26:EES-EAI:WH_BLF:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.74 | P13:345,24:CLEC::G1DOLHILL::1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.81 | P12:EHV:EES::8ANO%:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.84 | P11:22:EES-EAI:ARK_NU:1:D395 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.92 | P11:21:EES:RVB:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.92 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.92 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.94 | P11:HV:EES::1LEWIS_U3 ST:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.96 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 126.96 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 127.01 | P11:25:EES:WATERF:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 127.01 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 127.01 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 127.33 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 127.33 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 127.33 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 127.39 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 127.39 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 127.45 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 128 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 128.77 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 130.63 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21621 | 131.12 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21622 | 126.1 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21622 | 126.1 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21623 | 126.09 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21627 | 126.14 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21627 | 126.14 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 126.25 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 126.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 126.26 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21631 | 125.72 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21631 | 126.29 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21631 | 126.3 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2164 | 126.2 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21641 | 126.39 | P23:345:WERE:WICH-345-50:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21647 | 126.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21661 | 126.58 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21663 | 126.49 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21669 | 126.75 | P23:345:WERE:BUFF-345-534:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21669 | 126.75 | P23:345:WERE:BUFF-345-543:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21672 | 126.26 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2172 | 128.46 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21728 | 128 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21732 | 128.18 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21733 | 127.38 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21733 | 127.38 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2175 | 127.78 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21751 | 127.03 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21751 | 127.08 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21823 | 128.37 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21823 | 128.58 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21827 | 128.71 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21827 | 128.72 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21831 | 127.5 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21863 | 128.45 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21995 | 130.56 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21998 | 130.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22004 | 130.51 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22021 | 130.68 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22041 | 128.69 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22041 | 128.69 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22137 | 133.73 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22148 | 128.3 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22188 | 133.15 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22262 | 133.73 | POI 515800_22 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22262 | 133.85 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22472 | 139.88 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22618 | 155.33 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22724 | 148.52 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22724 | 151.14 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22724 | 152.15 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22724 | 154.71 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22724 | 155.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22724 | 155.72 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22724 | 155.73 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22724 | 155.73 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22741 | 138.8 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22741 | 139.72 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23061 | 136.37 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23061 | 138.58 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23061 | 138.58 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35803 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20097 | 118.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20097 | 120.77 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20097 | 120.78 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.34543 | 203.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 185 | 210 | 1 | 133.27 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 185 | 210 | 1 | 132.5 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1 | TDF Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2113 | 187.51 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21233 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21233 | 188.56 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21233 | 188.56 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21233 | 196.01 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2167 | 188.69 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21108 | 188.08 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21211 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21211 | 189.17 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21211 | 189.17 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21211 | 196.69 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21649 | 189.3 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.20345 | 103.2 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.20608 | 121.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525549 TOLK 7 345 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.20345 | 103.84 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.20608 | 122.42 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20093 | 151.79 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 145.67 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 147.96 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 148.9 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 151.28 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 134.4 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 136.62 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 136.62 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29198 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.2817 | 203.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.09 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.1 | P11:21:EES:RVB:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.12 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.18 | P11:25:EES:WATERF:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.18 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.18 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21945 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22059 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22071 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22076 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22077 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22077 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22096 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22101 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22102 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22102 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22158 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22158 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22215 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22228 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22267 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22268 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22274 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22279 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22279 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22389 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22452 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22464 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22489 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22493 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22496 | 103.51 | Potential P4 Event - POI 523823_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22648 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22723 | 106.63 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2273 | 106.08 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2273 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22908 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23886 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24614 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24614 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24614 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26059 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37603 | 159.35 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41286 | 188.69 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4143 | 187.51 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 188.56 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 188.56 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 196.01 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21915 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23909 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.3757 | 160.18 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41245 | 189.3 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41387 | 188.08 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 189.17 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 189.17 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 196.69 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20093 | 155.33 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 148.52 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 151.14 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.15 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 154.71 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.72 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.73 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.73 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 136.37 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 138.58 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 138.58 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29198 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.2817 | 203.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.20345 | 103.2 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.20608 | 121.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525549 TOLK 7 345 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.20345 | 103.84 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.20608 | 122.42 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20093 | 151.79 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 145.67 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 147.96 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 148.9 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 151.28 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 134.4 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 136.62 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 136.62 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29198 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.2817 | 203.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.09 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.1 | P11:21:EES:RVB:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.12 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.18 | P11:25:EES:WATERF:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.18 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.18 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21945 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22059 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22071 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22076 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22077 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22077 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22096 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22101 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22102 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22102 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22158 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22158 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22215 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22228 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22267 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22268 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22274 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22279 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22279 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22389 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22452 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22464 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22489 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22493 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22496 | 103.51 | Potential P4 Event - POI 523823_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22648 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22723 | 106.63 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2273 | 106.08 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2273 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22908 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23886 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24614 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24614 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24614 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26059 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37603 | 159.35 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41286 | 188.69 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4143 | 187.51 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 188.56 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 188.56 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 196.01 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21915 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23909 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.3757 | 160.18 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41245 | 189.3 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41387 | 188.08 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 189.17 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 189.17 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 196.69 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20093 | 155.33 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 148.52 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 151.14 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.15 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 154.71 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.72 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.73 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.73 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 136.37 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 138.58 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 138.58 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29198 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.2817 | 203.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21826 | 169.96 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21826 | 171.98 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21826 | 171.99 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21841 | 172.27 | Potential P4 Event - POI 527656_13 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21841 | 172.27 | Potential P4 Event - POI 527656_14 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21869 | 172.75 | Potential P4 Event - POI 527656_0 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.2153 | 103.2 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21807 | 121.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525549 TOLK 7 345 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.2153 | 103.84 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21807 | 122.42 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20346 | 134.4 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20346 | 136.62 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20346 | 136.62 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.27533 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.26564 | 203.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.09 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.1 | P11:21:EES:RVB:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.12 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.18 | P11:25:EES:WATERF:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.18 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.18 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22306 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22318 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22321 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22321 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22323 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22325 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22325 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22344 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22348 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2235 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2235 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22432 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22435 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22463 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22483 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22483 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22518 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22519 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22522 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22697 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22709 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22734 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22738 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22741 | 103.51 | Potential P4 Event - POI 523823_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22786 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2288 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22966 | 106.63 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22973 | 106.08 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22973 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23153 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24161 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2502 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2502 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2502 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.27028 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.36974 | 159.35 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4174 | 188.69 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41898 | 187.51 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42271 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42271 | 188.56 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42271 | 188.56 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42271 | 196.01 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22167 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24798 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.36942 | 160.18 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41699 | 189.3 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41856 | 188.08 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42227 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42227 | 189.17 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42227 | 189.17 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42227 | 196.69 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20346 | 136.37 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20346 | 138.58 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20346 | 138.58 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.27533 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.26564 | 203.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21826 | 169.96 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21826 | 171.98 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21826 | 171.99 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21841 | 172.27 | Potential P4 Event - POI 527656_13 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21841 | 172.27 | Potential P4 Event - POI 527656_14 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21869 | 172.75 | Potential P4 Event - POI 527656_0 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.2153 | 103.2 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21807 | 121.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525549 TOLK 7 345 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.2153 | 103.84 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21807 | 122.42 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20346 | 134.4 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20346 | 136.62 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20346 | 136.62 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.27533 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.26564 | 203.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.09 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.1 | P11:21:EES:RVB:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.12 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.18 | P11:25:EES:WATERF:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.18 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.18 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22167 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22306 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22318 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22321 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22321 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22323 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22325 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22325 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22344 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22348 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2235 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2235 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22432 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22435 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22463 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22483 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22483 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22518 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22519 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22522 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22697 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22709 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22734 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22738 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22741 | 103.51 | Potential P4 Event - POI 523823_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22786 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2288 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22966 | 106.63 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22973 | 106.08 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22973 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23153 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24161 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2502 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2502 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2502 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.27028 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.36974 | 159.35 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4174 | 188.69 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41898 | 187.51 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42271 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42271 | 188.56 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42271 | 188.56 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42271 | 196.01 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22167 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24798 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.36942 | 160.18 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41699 | 189.3 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41856 | 188.08 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42227 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42227 | 189.17 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42227 | 189.17 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42227 | 196.69 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20346 | 136.37 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20346 | 138.58 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20346 | 138.58 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.27533 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.26564 | 203.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.20345 | 103.2 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.20608 | 121.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525549 TOLK 7 345 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.20345 | 103.84 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.20608 | 122.42 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20093 | 151.79 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 145.67 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 147.96 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 148.9 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 151.28 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 134.4 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 136.62 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 136.62 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29198 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.2817 | 203.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.09 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.1 | P11:21:EES:RVB:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.12 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.18 | P11:25:EES:WATERF:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.18 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.18 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21945 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22059 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22071 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22076 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22077 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22077 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22096 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22101 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22102 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22102 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22158 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22158 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22215 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22228 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22267 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22268 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22274 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22279 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22279 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22389 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22452 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22464 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22489 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22493 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22496 | 103.51 | Potential P4 Event - POI 523823_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22648 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22723 | 106.63 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2273 | 106.08 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2273 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22908 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23886 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24614 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24614 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24614 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26059 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37603 | 159.35 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41286 | 188.69 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4143 | 187.51 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 188.56 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 188.56 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 196.01 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21915 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23909 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.3757 | 160.18 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41245 | 189.3 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41387 | 188.08 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 189.17 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 189.17 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 196.69 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20093 | 155.33 | Potential P4 Event - POI 525832_7 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 148.52 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 151.14 | Potential P4 Event - POI 764945_0 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.15 | Potential P4 Event - POI 764945_1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 154.71 | Potential P4 Event - POI 764945_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.72 | Potential P4 Event - POI 525832_2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.73 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.73 | Potential P4 Event - POI 525832_9 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 136.37 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 138.58 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 138.58 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29198 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.2817 | 203.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20962 | 169.96 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20962 | 171.98 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20962 | 171.99 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20975 | 172.27 | Potential P4 Event - POI 527656_13 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20975 | 172.27 | Potential P4 Event - POI 527656_14 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21007 | 172.75 | Potential P4 Event - POI 527656_0 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.20211 | 121.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.20211 | 122.42 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2002 | 134.4 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2002 | 136.62 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2002 | 136.62 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.27444 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.26478 | 203.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21145 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.09 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.1 | P11:21:EES:RVB:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.12 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.18 | P11:25:EES:WATERF:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.18 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.18 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.214 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21543 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21555 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21559 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2156 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2156 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21578 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21578 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21582 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21585 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21585 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21585 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21687 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21699 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21737 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21737 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21758 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21764 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21765 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21937 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21949 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21975 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21978 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21982 | 103.51 | Potential P4 Event - POI 523823_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22068 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22138 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2221 | 106.63 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22217 | 106.08 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22217 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22414 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23459 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24045 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24045 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24045 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26256 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.36152 | 159.35 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.40353 | 188.69 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.40456 | 187.51 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.40809 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.40809 | 188.56 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.40809 | 188.56 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.40809 | 196.01 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21523 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2409 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.36121 | 160.18 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.40313 | 189.3 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.40415 | 188.08 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.40767 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.40767 | 189.17 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.40767 | 189.17 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.40767 | 196.69 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2002 | 136.37 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2002 | 138.58 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2002 | 138.58 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.27444 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.26478 | 203.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20852 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2395 | 159.35 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2602 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.30529 | 187.51 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.30746 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.30746 | 188.56 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.30746 | 188.56 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.30746 | 196.01 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.30823 | 188.69 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23873 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23929 | 160.18 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.30497 | 188.08 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.30715 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.30715 | 189.17 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.30715 | 189.17 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.30715 | 196.69 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.30792 | 189.3 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22479 | 169.96 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22479 | 171.98 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22479 | 171.99 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22492 | 172.27 | Potential P4 Event - POI 527656_13 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22492 | 172.27 | Potential P4 Event - POI 527656_14 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.2252 | 172.75 | Potential P4 Event - POI 527656_0 | TDF Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.22112 | 103.2 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.22397 | 121.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525549 TOLK 7 345 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.22112 | 103.84 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.22397 | 122.42 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | TDF Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20797 | 134.4 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20797 | 136.62 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20797 | 136.62 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.28114 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.27125 | 203.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.09 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.1 | P11:21:EES:RVB:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.12 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.18 | P11:25:EES:WATERF:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.18 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.18 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21674 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21816 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21828 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21832 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21834 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21834 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2185 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2185 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21855 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21858 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21859 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21859 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21956 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21972 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22007 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22007 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22032 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22033 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22034 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22209 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22221 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22247 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2225 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22253 | 103.51 | Potential P4 Event - POI 523823_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22261 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22404 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2248 | 106.63 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22487 | 106.08 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22487 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22678 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23706 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24605 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24605 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24605 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26463 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.36784 | 159.35 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.40849 | 188.69 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.40972 | 187.51 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41332 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41332 | 188.56 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41332 | 188.56 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41332 | 196.01 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2175 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2428 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.36752 | 160.18 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.40809 | 189.3 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4093 | 188.08 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41289 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41289 | 189.17 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41289 | 189.17 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41289 | 196.69 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20797 | 136.37 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20797 | 138.58 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20797 | 138.58 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.28114 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.27125 | 203.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20079 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20807 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26487 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26576 | 159.35 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34549 | 187.51 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34685 | 188.69 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34821 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34821 | 188.56 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34821 | 188.56 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34821 | 196.01 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24302 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.26553 | 160.18 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.34514 | 188.08 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.34651 | 189.3 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.34785 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.34785 | 189.17 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.34785 | 189.17 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.34785 | 196.69 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21147 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21147 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21147 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21489 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21489 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.09 | P12:EHV:EES::8ANO%:1(1) | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.1 | P11:21:EES:RVB:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.12 | P11:EHV:EES::1ANO U2:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.18 | P11:25:EES:WATERF:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.18 | P11:HV:EES::1WAT U3!:1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.18 | P13:230:EES:WATERF:T6:T7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21512 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21652 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21664 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21668 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21671 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21671 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21694 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21695 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21695 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21696 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21696 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21746 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21746 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21811 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21815 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2187 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21888 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2189 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22043 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22055 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22081 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22084 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22088 | 103.51 | Potential P4 Event - POI 523823_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22222 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22313 | 106.63 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2232 | 106.08 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2232 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22534 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23356 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23684 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28391 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.30922 | 159.35 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.40565 | 188.69 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.40667 | 187.51 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41022 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41022 | 188.56 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41022 | 188.56 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41022 | 196.01 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2173 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.26049 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.30895 | 160.18 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.40525 | 189.3 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.40625 | 188.08 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4098 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4098 | 189.17 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4098 | 189.17 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4098 | 196.69 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21303 | 159.35 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23593 | 187.51 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23723 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23723 | 188.56 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23723 | 188.56 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23723 | 196.01 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24089 | 188.69 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21284 | 160.18 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23569 | 188.08 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23699 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23699 | 189.17 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23699 | 189.17 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23699 | 196.69 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24065 | 189.3 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23162 | 159.35 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25413 | 187.51 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25567 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25567 | 188.56 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25567 | 188.56 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25567 | 196.01 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25844 | 188.69 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23142 | 160.18 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25387 | 188.08 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2554 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2554 | 189.17 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2554 | 189.17 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2554 | 196.69 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25819 | 189.3 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2006 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20118 | 106.63 | Potential P4 Event - POI 523823_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20125 | 106.08 | Potential P4 Event - POI 523823_11 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20125 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20398 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21451 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21725 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.27231 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.27464 | 159.35 | Potential P4 Event - POI 525832_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28633 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.3649 | 187.51 | Potential P4 Event - POI 560022_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.36551 | 188.69 | Potential P4 Event - POI 560022_7 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.36789 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.36789 | 188.56 | Potential P4 Event - POI 525832_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.36789 | 188.56 | Potential P4 Event - POI 525832_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.36789 | 196.01 | Potential P4 Event - POI 560022_8 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24984 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2744 | 160.18 | Potential P4 Event - POI 525832_5 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.36453 | 188.08 | Potential P4 Event - POI 560022_1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.36515 | 189.3 | Potential P4 Event - POI 560022_3 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.36751 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.36751 | 189.17 | Potential P4 Event - POI 525832_0 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.36751 | 189.17 | Potential P4 Event - POI 525832_6 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.36751 | 196.69 | Potential P4 Event - POI 560022_4 | TDF Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05112 | 141.57 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05112 | 140.52 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12267 | 108.49 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12267 | 108.49 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09089 | 105.19 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09097 | 106.48 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09097 | 106.5 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09121 | 103.66 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09123 | 106.75 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0913 | 104.31 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0913 | 106.39 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09147 | 103.96 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09151 | 103.86 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09164 | 103.86 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09166 | 104.29 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09166 | 104.3 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09168 | 104.25 | P11:18:HAST::EGYCTR2G WEC2:LOSS OF WEC 2 GEN:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09168 | 104.25 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09171 | 103.62 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09175 | 103.95 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0918 | 104.21 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09184 | 103.7 | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 103.19 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 103.19 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 103.2 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 103.22 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 103.36 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 103.65 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 103.87 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 103.87 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 103.87 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 103.87 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 103.87 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 103.94 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 103.95 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 104.01 | P13:NBEC#1 GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 104.1 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 104.18 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 104.28 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 104.31 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 104.65 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 104.66 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 104.71 | 531504 CIMWD2 7 345 3WXFMR CIMRNWND2 MPT 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 104.71 | GEN-2010-009_POI_531501_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 104.74 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 104.75 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 104.75 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 104.75 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 104.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 104.87 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 104.87 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 105.04 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 105.14 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 105.15 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 105.37 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 105.37 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 105.49 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 105.49 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 105.51 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 105.53 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 105.64 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 105.65 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 105.72 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 105.74 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 105.88 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 105.91 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09188 | 111.31 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09189 | 103.33 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09189 | 105.63 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0919 | 103.48 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09192 | 103.3 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09192 | 103.41 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09192 | 103.46 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09192 | 103.48 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09193 | 103.26 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09193 | 103.62 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09193 | 103.92 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09193 | 103.92 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09193 | 103.97 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09195 | 104.56 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09196 | 103.43 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09198 | 103.92 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09198 | 104.02 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09199 | 103.51 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.092 | 104.19 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09201 | 103.93 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09201 | 104.29 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09203 | 104.28 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09205 | 103.85 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09206 | 103.53 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09206 | 103.72 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09206 | 104.21 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09206 | 104.21 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09207 | 103.77 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09209 | 104.04 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09211 | 103.96 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09213 | 105.27 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09215 | 105.48 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09216 | 103.57 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09216 | 104.43 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09239 | 103.64 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09239 | 104.27 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 104.71 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09244 | 104.71 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09246 | 104.64 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09247 | 104.3 | P12:345:WERE:VIOL-WICH-345:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09249 | 104.04 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09283 | 104.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09301 | 104.54 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09311 | 104.7 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09311 | 104.71 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09315 | 106 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09319 | 111.68 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09327 | 104.05 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09356 | 104.72 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09356 | 104.73 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0936 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0936 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0936 | 105.45 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09364 | 104.85 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09364 | 104.85 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09365 | 104.84 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09368 | 106.71 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09442 | 106.03 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0945 | 105.86 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09484 | 106.65 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09484 | 106.7 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09579 | 109.43 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09619 | 107.32 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09619 | 107.46 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09619 | 107.57 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09619 | 109.51 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09663 | 104.64 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09663 | 105.34 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09817 | 108.97 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10053 | 111.96 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10246 | 109.15 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1027 | 120.22 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1027 | 120.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1027 | 120.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1027 | 120.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1027 | 120.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11281 | 124.48 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11281 | 124.48 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11281 | 124.48 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11814 | 126.32 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11814 | 126.32 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11814 | 126.32 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12006 | 135.92 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12006 | 135.92 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10531 | 106.45 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10531 | 106.46 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10531 | 106.46 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10531 | 106.46 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10531 | 106.46 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11542 | 110.51 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11542 | 110.51 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11542 | 110.51 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12075 | 112.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12075 | 112.81 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12075 | 112.81 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12267 | 122.53 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12267 | 122.53 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0564 | 188.65 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0564 | 190.26 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.06034 | 111.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.07957 | 115.99 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06021 | 139.19 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06028 | 143.07 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06045 | 138.87 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06312 | 135.64 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06312 | 135.64 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06315 | 135.15 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06319 | 135.16 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06322 | 135.07 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.02 | 562727 LESBIA 115 562728 SANJONTAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.07 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.14 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.15 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.17 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.38 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.38 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.44 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.47 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.47 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.48 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.49 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.52 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.52 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.52 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.52 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.55 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.55 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.57 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.59 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.62 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.62 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.7 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.7 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.7 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.7 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.72 | P11:26:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.72 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.72 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.73 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.73 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.73 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.75 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.75 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.76 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.77 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.78 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.83 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.95 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.95 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.95 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.95 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.95 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.98 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 135.98 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 136 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 136.02 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 136.02 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 136.02 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 136.24 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 136.24 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 136.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 136.47 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 136.47 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 136.47 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 137.36 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06323 | 139.3 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06324 | 135.15 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06326 | 135.16 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06327 | 135.15 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06327 | 135.15 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06327 | 135.15 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06327 | 135.39 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06327 | 135.44 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06328 | 135.45 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06329 | 135.02 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06329 | 135.49 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06329 | 135.56 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06329 | 135.56 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06335 | 135.63 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06335 | 135.65 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06335 | 135.73 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06336 | 135.61 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06339 | 135.62 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06344 | 136 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06348 | 135.63 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06351 | 135.96 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06351 | 135.96 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06378 | 137.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0638 | 137.43 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0638 | 137.43 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06382 | 137.34 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06388 | 137.04 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06388 | 137.04 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06388 | 137.06 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06388 | 137.16 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06388 | 137.41 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06388 | 137.41 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06399 | 137.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06405 | 139.39 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06408 | 136.61 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06445 | 138.33 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06467 | 137.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0651 | 137.58 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06511 | 137.59 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06534 | 141.34 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06537 | 141.38 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06546 | 141.62 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06546 | 141.62 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0663 | 141.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06796 | 142.78 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06796 | 142.94 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07398 | 149.61 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07422 | 147.71 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07422 | 148.81 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08556 | 152.28 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08556 | 159.07 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08556 | 161.78 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08556 | 163.27 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.10845 | 163.49 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07334 | 119.52 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07334 | 119.53 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08331 | 118.97 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08923 | 109.05 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08923 | 109.05 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08942 | 108.48 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08942 | 108.48 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08944 | 108.65 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08944 | 108.87 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.39 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.46 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.48 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.48 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.64 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.64 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.67 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.67 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.79 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.82 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.82 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.87 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.89 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.9 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.9 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.92 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.94 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.94 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.99 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.99 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.03 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.04 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.14 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.15 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.15 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.16 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.17 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.17 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.17 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.18 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.18 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.18 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.22 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.22 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.23 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.24 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.26 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.3 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.37 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.4 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.49 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.49 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.49 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.49 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.49 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.53 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.53 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.53 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.58 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.58 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.59 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.69 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.69 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.69 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.75 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.75 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.78 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 110.66 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 110.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 111.04 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 111.24 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 113.28 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08951 | 108.45 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08951 | 108.45 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08951 | 108.45 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08953 | 108.69 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08953 | 108.76 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08955 | 108.28 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08955 | 108.77 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08956 | 108.82 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08956 | 108.9 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08956 | 108.9 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08968 | 108.98 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08969 | 108.95 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08974 | 108.99 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08976 | 109.13 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08976 | 109.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08985 | 109.44 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08993 | 108.99 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08998 | 109.39 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08998 | 109.39 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09052 | 111.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09052 | 111.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09059 | 111.09 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09068 | 110.71 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09068 | 110.82 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09069 | 110.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09069 | 110.68 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0909 | 110.77 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09097 | 110.1 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09109 | 113.28 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09139 | 112.35 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09139 | 112.35 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09163 | 112.1 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09202 | 111.42 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09264 | 111.03 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09265 | 111.04 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09343 | 115.8 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09349 | 115.86 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09366 | 116.15 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09366 | 116.15 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09538 | 116.25 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09541 | 117.38 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09791 | 117.14 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09791 | 117.29 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10781 | 121.61 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10781 | 122.52 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13115 | 138.42 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13177 | 128.24 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13177 | 131.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13177 | 135.41 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13177 | 135.88 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13177 | 138.79 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13177 | 139.6 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13177 | 139.63 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13177 | 140.37 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13723 | 124.23 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14823 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06391 | 104.17 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06391 | 104.17 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0726 | 103.69 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08142 | 100.92 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08148 | 100.97 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08162 | 101.22 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08162 | 101.22 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08312 | 101.31 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08314 | 102.3 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08532 | 102.08 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08532 | 102.22 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09395 | 105.99 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09395 | 106.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1143 | 120.63 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11483 | 111.76 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11483 | 115 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11483 | 118.01 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11483 | 118.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11483 | 120.96 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11483 | 121.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11483 | 121.68 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11483 | 122.33 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11959 | 108.27 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14304 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.05843 | 102.88 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14397 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15293 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15391 | 104.54 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16004 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16532 | 100.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16532 | 100.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16532 | 100.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16532 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16532 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16532 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16532 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16532 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16532 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16532 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16532 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16532 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16532 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16532 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16683 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16683 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16691 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16705 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16705 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16706 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16706 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16723 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16736 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16753 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16757 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16757 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16849 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16906 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17007 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17008 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17095 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17103 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17119 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17125 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17126 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17361 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17371 | 107.18 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17377 | 106.47 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17377 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17764 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19304 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21061 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24545 | 154.86 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26476 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31305 | 187.42 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31526 | 183.57 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31526 | 183.59 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31526 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31526 | 195.61 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31601 | 188.13 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.17711 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24292 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24524 | 155.38 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31273 | 187.81 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31493 | 184.02 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31493 | 184.11 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31493 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31493 | 196.06 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.3157 | 188.56 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07334 | 118.53 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07334 | 120.63 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07334 | 120.63 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08331 | 119.68 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08797 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08923 | 109.42 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08923 | 109.42 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08942 | 108.86 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08942 | 108.86 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08944 | 109.03 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08944 | 109.24 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.77 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.83 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.84 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.86 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 108.86 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.02 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.02 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.07 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.07 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.17 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.19 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.19 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.25 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.27 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.27 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.27 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.29 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.31 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.31 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.36 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.36 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.4 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.41 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.51 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.52 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.52 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.53 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.54 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.54 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.54 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.54 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.55 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.55 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.59 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.59 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.6 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.6 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.62 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.66 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.73 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.77 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.85 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.85 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.85 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.85 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.85 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.89 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.89 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.9 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.95 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.95 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 109.95 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 110.17 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 110.17 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 110.17 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 110.25 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 110.25 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 110.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 111.11 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 111.53 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 111.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08945 | 114.16 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08951 | 108.84 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08951 | 108.84 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08951 | 108.84 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08953 | 109.07 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08953 | 109.14 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08955 | 108.67 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08955 | 109.14 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08956 | 109.19 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08956 | 109.27 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08956 | 109.27 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08968 | 109.35 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08969 | 109.33 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08974 | 109.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08976 | 109.5 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08976 | 109.62 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08985 | 109.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08993 | 109.36 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08998 | 109.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08998 | 109.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09052 | 111.45 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09052 | 111.45 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09059 | 111.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09068 | 111.03 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09068 | 111.14 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09069 | 111 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09069 | 111 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0909 | 111.06 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09097 | 110.42 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09109 | 113.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09139 | 112.76 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09139 | 112.76 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09163 | 112.34 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09202 | 111.7 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09264 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09265 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09343 | 116 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09349 | 116.05 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09366 | 116.33 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09366 | 116.33 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09538 | 116.57 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09791 | 117.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09791 | 117.33 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10781 | 121.98 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10781 | 122.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13115 | 141.25 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13177 | 130.11 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13177 | 134.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13177 | 137.98 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13177 | 138.46 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13177 | 141.54 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13177 | 142.35 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13177 | 142.4 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13177 | 143.16 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13723 | 124.63 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14823 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06391 | 103.3 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06391 | 105.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06391 | 105.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0726 | 104.3 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08142 | 101.1 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08148 | 101.14 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08162 | 101.39 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08162 | 101.39 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08312 | 101.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08532 | 102.12 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08532 | 102.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09395 | 106.31 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09395 | 107.11 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1143 | 123.1 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11483 | 113.4 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11483 | 117.19 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11483 | 120.26 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11483 | 120.67 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11483 | 123.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11483 | 124.06 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11483 | 124.1 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11483 | 124.76 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11959 | 108.62 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14304 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.06883 | 112.72 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08342 | 119.45 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08367 | 106.79 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08367 | 109.48 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08367 | 114.6 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08367 | 115.27 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08367 | 119.86 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08367 | 120.54 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08367 | 120.55 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08367 | 121.12 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | ASGI-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09463 | 111.33 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1172 | 108.49 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1172 | 108.49 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0862 | 105.19 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08628 | 106.48 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08629 | 106.5 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08653 | 103.66 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08654 | 106.75 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08661 | 104.31 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08661 | 106.39 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08678 | 103.96 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08682 | 103.86 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08695 | 103.86 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08697 | 104.29 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08697 | 104.3 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.087 | 104.25 | P11:18:HAST::EGYCTR2G WEC2:LOSS OF WEC 2 GEN:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.087 | 104.25 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08702 | 103.62 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08707 | 103.95 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08711 | 104.21 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08715 | 103.7 | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 103.19 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 103.19 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 103.22 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 103.36 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 103.65 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 103.87 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 103.87 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 103.87 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 103.87 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 103.87 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 103.94 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 103.95 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 104.01 | P13:NBEC#1 GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 104.1 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 104.18 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 104.28 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 104.31 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 104.65 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 104.66 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 104.71 | 531504 CIMWD2 7 345 3WXFMR CIMRNWND2 MPT 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 104.71 | GEN-2010-009_POI_531501_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 104.74 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 104.75 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 104.75 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 104.75 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 104.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 104.87 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 104.87 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 105.04 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 105.14 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 105.15 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 105.37 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 105.37 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 105.49 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 105.49 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 105.51 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 105.53 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 105.64 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 105.65 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 105.72 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 105.74 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 105.88 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 105.91 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08719 | 111.31 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0872 | 103.2 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0872 | 103.33 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0872 | 105.63 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08721 | 103.48 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08723 | 103.46 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08723 | 103.48 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08724 | 103.3 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08724 | 103.41 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08724 | 103.92 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08724 | 103.92 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08724 | 103.97 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08725 | 103.26 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08725 | 103.62 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08726 | 104.56 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08727 | 103.43 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0873 | 103.51 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0873 | 103.92 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0873 | 104.02 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08732 | 103.93 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08732 | 104.19 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08733 | 104.29 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08735 | 104.28 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08736 | 103.85 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08737 | 104.21 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08737 | 104.21 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08738 | 103.53 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08738 | 103.72 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08739 | 103.77 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08741 | 104.04 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08744 | 103.96 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08746 | 105.27 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08748 | 103.57 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08748 | 104.43 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08748 | 105.48 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08772 | 103.64 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08774 | 104.27 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08778 | 104.71 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08778 | 104.71 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08781 | 104.64 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08783 | 104.04 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08783 | 104.3 | P12:345:WERE:VIOL-WICH-345:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08817 | 104.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08832 | 104.7 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08832 | 104.71 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08839 | 104.54 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08846 | 111.68 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08853 | 106 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08856 | 104.05 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08891 | 104.72 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08891 | 104.73 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08902 | 104.85 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08902 | 104.85 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08905 | 104.84 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08908 | 106.71 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08913 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08913 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08913 | 105.45 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08978 | 106.03 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0898 | 106.65 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0898 | 106.7 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08986 | 105.86 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09091 | 109.43 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0913 | 107.32 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0913 | 107.46 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0913 | 107.57 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0913 | 109.51 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09274 | 108.97 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09346 | 104.64 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09346 | 105.34 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09559 | 111.96 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09605 | 109.15 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09749 | 120.22 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09749 | 120.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09749 | 120.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09749 | 120.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09749 | 120.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10566 | 124.48 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10566 | 124.48 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10566 | 124.48 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11261 | 126.32 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11261 | 126.32 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11261 | 126.32 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1146 | 135.92 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1146 | 135.92 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1001 | 106.45 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1001 | 106.46 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1001 | 106.46 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1001 | 106.46 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1001 | 106.46 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10827 | 110.51 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10827 | 110.51 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10827 | 110.51 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11521 | 112.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11521 | 112.81 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11521 | 112.81 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1172 | 122.53 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1172 | 122.53 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06454 | 188.65 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06454 | 190.26 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.06076 | 111.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.05024 | 106.67 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.07724 | 115.99 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0501 | 162.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0501 | 164.73 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0501 | 164.73 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0501 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0505 | 165.04 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0505 | 165.04 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05128 | 165.64 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0513 | 164.89 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05341 | 143.07 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06027 | 139.19 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0604 | 138.87 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0618 | 135.64 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0618 | 135.64 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06183 | 135.15 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06187 | 135.16 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0619 | 135.07 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.02 | 562727 LESBIA 115 562728 SANJONTAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.07 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.14 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.15 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.17 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.38 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.38 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.44 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.47 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.47 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.48 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.49 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.52 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.52 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.52 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.52 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.55 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.55 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.57 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.59 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.62 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.62 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.7 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.7 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.7 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.7 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.72 | P11:26:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.72 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.72 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.73 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.73 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.73 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.75 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.75 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.76 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.77 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.78 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.83 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.95 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.95 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.95 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.95 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.95 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.98 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 135.98 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 136 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 136.02 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 136.02 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 136.02 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 136.24 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 136.24 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 136.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 136.47 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 136.47 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 136.47 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 137.36 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06191 | 139.3 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06192 | 135.15 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06195 | 135.15 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06195 | 135.15 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06195 | 135.15 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06195 | 135.16 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06195 | 135.39 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06196 | 135.44 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06196 | 135.45 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06197 | 135.02 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06197 | 135.49 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06197 | 135.56 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06197 | 135.56 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06203 | 135.63 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06203 | 135.65 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06203 | 135.73 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06204 | 135.61 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06207 | 135.62 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06212 | 136 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06216 | 135.63 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06218 | 135.96 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06218 | 135.96 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06246 | 137.34 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06246 | 137.43 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06246 | 137.43 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06249 | 137.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06252 | 137.04 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06252 | 137.04 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06254 | 137.06 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06254 | 137.16 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06258 | 137.41 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06258 | 137.41 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06261 | 137.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06266 | 136.61 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06276 | 139.39 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0631 | 138.33 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0633 | 137.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06349 | 137.58 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06349 | 137.59 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06391 | 141.34 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06394 | 141.38 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06403 | 141.62 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06403 | 141.62 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06463 | 141.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06608 | 142.78 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06608 | 142.94 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07111 | 147.71 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07111 | 148.81 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07654 | 149.61 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09133 | 152.28 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09133 | 159.07 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09133 | 161.78 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09133 | 163.27 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09702 | 163.49 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09438 | 119.52 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09438 | 119.53 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10055 | 118.97 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1029 | 109.05 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1029 | 109.05 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1031 | 108.48 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1031 | 108.48 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10312 | 108.48 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10312 | 108.65 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10312 | 108.87 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 108.39 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 108.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 108.46 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 108.48 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 108.64 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 108.64 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 108.67 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 108.67 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 108.79 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 108.82 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 108.82 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 108.87 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 108.89 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 108.9 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 108.9 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 108.92 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 108.94 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 108.94 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 108.99 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 108.99 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.03 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.04 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.14 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.15 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.15 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.16 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.17 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.17 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.17 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.18 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.18 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.18 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.22 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.22 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.23 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.24 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.26 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.3 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.37 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.4 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.49 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.49 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.49 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.49 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.49 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.53 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.53 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.53 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.58 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.58 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.59 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.69 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.69 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.69 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.75 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.75 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.78 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 110.66 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 110.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 111.04 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 111.24 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 113.28 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10319 | 108.45 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10319 | 108.45 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10319 | 108.45 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1032 | 108.69 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10321 | 108.76 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10322 | 108.28 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10322 | 108.77 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10323 | 108.82 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10323 | 108.9 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10323 | 108.9 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10334 | 108.98 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10335 | 108.95 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10341 | 108.99 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10342 | 109.13 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10342 | 109.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10351 | 109.44 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10359 | 108.99 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10363 | 109.39 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10363 | 109.39 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10416 | 111.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10416 | 111.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10417 | 111.09 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10428 | 110.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10428 | 110.68 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10431 | 110.71 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10431 | 110.82 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10446 | 110.77 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10447 | 110.1 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10483 | 113.28 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10513 | 112.35 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10513 | 112.35 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10524 | 112.1 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10562 | 111.42 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10581 | 111.03 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10581 | 111.04 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1069 | 115.8 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10696 | 115.86 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10712 | 116.15 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10712 | 116.15 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10836 | 116.25 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10879 | 117.38 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11058 | 117.14 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11058 | 117.29 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11849 | 121.61 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11849 | 122.52 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14023 | 124.23 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15814 | 138.42 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15887 | 128.24 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15887 | 131.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15887 | 135.41 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15887 | 135.88 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15887 | 138.79 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15887 | 139.6 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15887 | 139.63 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15887 | 140.37 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17089 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08225 | 104.17 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08225 | 104.17 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08763 | 103.69 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09316 | 100.92 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09322 | 100.97 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09335 | 101.22 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09335 | 101.22 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09444 | 101.31 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0948 | 102.3 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09637 | 102.08 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09637 | 102.22 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10326 | 105.99 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10326 | 106.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12221 | 108.27 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13781 | 120.63 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13845 | 111.76 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13845 | 115 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13845 | 118.01 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13845 | 118.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13845 | 120.96 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13845 | 121.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13845 | 121.68 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13845 | 122.33 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1649 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09655 | 102.88 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1923 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1967 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19942 | 104.54 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20122 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20343 | 100.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20343 | 100.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20343 | 100.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20343 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20343 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20343 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20343 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20343 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20343 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20343 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20343 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20343 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20343 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20343 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20489 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20489 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2049 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20505 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20505 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2051 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2051 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20531 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20538 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20542 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20576 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20576 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20652 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20705 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20743 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20744 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20876 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20885 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20901 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20907 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20908 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21075 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21141 | 107.18 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21147 | 106.47 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21147 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21429 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22537 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22663 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28065 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.29595 | 154.86 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38476 | 187.42 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.3849 | 188.13 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38794 | 183.57 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38794 | 183.59 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38794 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38794 | 195.61 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.20793 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25749 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.29569 | 155.38 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38437 | 187.81 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38452 | 188.56 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38754 | 184.02 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38754 | 184.11 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38754 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38754 | 196.06 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09438 | 118.53 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09438 | 120.63 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09438 | 120.63 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09887 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10055 | 119.68 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1029 | 109.42 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1029 | 109.42 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1031 | 108.86 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1031 | 108.86 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10312 | 108.86 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10312 | 109.03 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10312 | 109.24 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 108.77 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 108.83 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 108.84 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 108.86 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.02 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.02 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.07 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.07 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.17 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.19 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.19 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.25 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.27 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.27 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.27 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.29 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.31 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.31 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.36 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.36 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.4 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.41 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.51 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.52 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.52 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.53 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.54 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.54 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.54 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.54 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.55 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.55 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.59 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.59 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.6 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.6 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.62 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.66 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.73 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.77 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.85 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.85 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.85 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.85 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.85 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.89 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.89 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.9 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.95 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.95 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 109.95 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 110.17 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 110.17 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 110.17 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 110.25 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 110.25 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 110.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 111.11 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 111.53 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 111.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10313 | 114.16 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10319 | 108.84 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10319 | 108.84 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10319 | 108.84 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1032 | 109.07 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10321 | 109.14 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10322 | 108.67 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10322 | 109.14 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10323 | 109.19 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10323 | 109.27 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10323 | 109.27 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10334 | 109.35 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10335 | 109.33 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10341 | 109.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10342 | 109.5 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10342 | 109.62 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10351 | 109.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10359 | 109.36 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10363 | 109.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10363 | 109.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10416 | 111.45 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10416 | 111.45 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10417 | 111.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10428 | 111 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10428 | 111 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10431 | 111.03 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10431 | 111.14 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10446 | 111.06 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10447 | 110.42 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10483 | 113.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10513 | 112.76 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10513 | 112.76 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10524 | 112.34 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10562 | 111.7 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10581 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10581 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1069 | 116 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10696 | 116.05 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10712 | 116.33 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10712 | 116.33 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10836 | 116.57 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11058 | 117.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11058 | 117.33 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11849 | 121.98 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11849 | 122.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14023 | 124.63 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15814 | 141.25 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15887 | 130.11 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15887 | 134.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15887 | 137.98 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15887 | 138.46 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15887 | 141.54 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15887 | 142.35 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15887 | 142.4 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15887 | 143.16 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17089 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08225 | 103.3 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08225 | 105.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08225 | 105.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08763 | 104.3 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09316 | 101.1 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09322 | 101.14 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09335 | 101.39 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09335 | 101.39 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09444 | 101.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09637 | 102.12 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09637 | 102.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10326 | 106.31 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10326 | 107.11 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12221 | 108.62 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13781 | 123.1 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13845 | 113.4 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13845 | 117.19 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13845 | 120.26 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13845 | 120.67 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13845 | 123.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13845 | 124.06 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13845 | 124.1 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13845 | 124.76 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1649 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08909 | 112.72 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10668 | 111.33 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.11241 | 119.45 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.11272 | 106.79 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.11272 | 109.48 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.11272 | 114.6 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.11272 | 115.27 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.11272 | 119.86 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.11272 | 120.54 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.11272 | 120.55 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.11272 | 121.12 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-001 | FROM->TO | 528413 TAYLOR 3 115 528449 W_BENDER 3 115 1 | 143 | 157 | 1 | 135.45 | 528355 MADDOX 3 115 762442 G18-004-TAP 115 1 | Cumulative Impact | Rebuild the existing TAYLOR3 to W_BENDER3 115 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | 353 | 353 | 0.05025 | 108.18 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing STLN-DEMARCO6 to G23-101-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1154 | 108.49 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1154 | 108.49 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08489 | 105.19 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08497 | 106.48 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08498 | 106.5 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 103.66 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 106.75 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0853 | 104.31 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0853 | 106.39 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08547 | 103.96 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08551 | 103.86 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08565 | 103.86 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08567 | 104.29 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08567 | 104.3 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08569 | 104.25 | P11:18:HAST::EGYCTR2G WEC2:LOSS OF WEC 2 GEN:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08569 | 104.25 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08571 | 103.62 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08576 | 103.95 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0858 | 104.21 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08584 | 103.7 | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.19 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.19 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.22 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.36 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.65 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.87 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.87 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.87 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.87 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.87 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.94 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.95 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.01 | P13:NBEC#1 GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.1 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.18 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.28 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.31 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.65 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.66 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.71 | 531504 CIMWD2 7 345 3WXFMR CIMRNWND2 MPT 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.71 | GEN-2010-009_POI_531501_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.74 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.75 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.75 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.75 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.87 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.87 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.04 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.14 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.15 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.37 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.37 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.49 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.49 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.51 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.53 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.64 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.65 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.72 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.74 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.88 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.91 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 111.31 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08589 | 103.2 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08589 | 103.33 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08589 | 105.63 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08591 | 103.48 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08592 | 103.46 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.3 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.41 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.48 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.92 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.92 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.97 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08594 | 103.26 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08594 | 103.62 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 104.56 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08596 | 103.43 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08599 | 103.92 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08599 | 104.02 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.086 | 103.51 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08601 | 104.19 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08602 | 103.93 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08602 | 104.29 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08604 | 104.28 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08605 | 103.85 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08606 | 104.21 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08606 | 104.21 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08607 | 103.53 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08608 | 103.72 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08609 | 103.77 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0861 | 104.04 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08614 | 103.96 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08615 | 105.27 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08617 | 105.48 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08618 | 103.57 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08618 | 104.43 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08641 | 103.64 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08644 | 104.27 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08649 | 104.71 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08649 | 104.71 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08652 | 104.64 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08653 | 104.3 | P12:345:WERE:VIOL-WICH-345:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08687 | 104.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08696 | 104.04 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08698 | 104.7 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08698 | 104.71 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08712 | 104.54 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08714 | 111.68 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08725 | 106 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08761 | 104.72 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08761 | 104.73 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08774 | 104.85 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08774 | 104.85 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08779 | 104.84 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08781 | 106.71 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08792 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08792 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08792 | 105.45 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08845 | 106.65 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08845 | 106.7 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08848 | 106.03 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08856 | 105.86 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08879 | 104.64 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08879 | 105.34 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08924 | 104.05 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08955 | 109.43 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08993 | 107.32 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08993 | 107.46 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08993 | 107.57 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08993 | 109.51 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09096 | 108.97 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09319 | 109.15 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09412 | 111.96 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09604 | 120.22 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09604 | 120.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09604 | 120.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09604 | 120.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09604 | 120.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10402 | 124.48 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10402 | 124.48 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10402 | 124.48 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11078 | 126.32 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11078 | 126.32 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11078 | 126.32 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1128 | 135.92 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1128 | 135.92 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09865 | 106.45 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09865 | 106.46 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09865 | 106.46 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09865 | 106.46 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09865 | 106.46 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10663 | 110.51 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10663 | 110.51 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10663 | 110.51 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11339 | 112.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11339 | 112.81 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11339 | 112.81 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1154 | 122.53 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1154 | 122.53 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09874 | 132.94 | P23:345:WERE:JEC-345-16:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09874 | 133 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09875 | 133.01 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09875 | 138.87 | Potential P4 Event - POI 773600_4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09876 | 138.88 | Potential P4 Event - POI 773600_7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09876 | 138.88 | Potential P4 Event - POI 773600_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09877 | 132.82 | 532792 FR2EAST7 345 588364 G16-153-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09877 | 132.87 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09878 | 132.62 | 514796 IODINE-4 138 515376 WWRDEHV4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09878 | 132.62 | 514796 IODINE-4 138 515533 REDCLFT4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09878 | 132.92 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09879 | 132.81 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09879 | 132.83 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09879 | 132.85 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0988 | 132.88 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0988 | 132.88 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0988 | 133.45 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09881 | 132.84 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.45 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.59 | 659387 KUMMERDG-BE3 345 659390 PATENTGT-BE3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.61 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.81 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.81 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.84 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.84 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.86 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.9 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.9 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.91 | P12:069:GLHP:COLE-TURPIN-BEARD-ADAMS-JEFFERSON:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.93 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.94 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.95 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.96 | ASGI-2023-001_POI_528252_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.96 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.96 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.96 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.98 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.99 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.99 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.99 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.99 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133 | P12:EHV:EES::8ISES%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133 | P23:345:XEL:8H14 PRI | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.01 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.01 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.04 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.04 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.04 | P23:500:EES-EAI:INDEP2:B6126 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.05 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.05 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.05 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.06 | P11:21:EES:RVB:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.06 | P11:HV:EES::1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.06 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.06 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.06 | P23:345:MEC:LOUISA 964 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.07 | P23:345:XEL:8N22 SHC | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P11:25:EES:WATERF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P23:345:MEC:CBEC 908 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.1 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.11 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.11 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.11 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.11 | P23:345:MEC:CBEC 905 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.15 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.18 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.19 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.19 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.21 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.28 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.3 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.47 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.76 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.88 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.24 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.42 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.43 | GEN-2023-201_POI_776000_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.91 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.91 | GEN-2023-236_POI_776700_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 138.67 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 138.67 | GEN-2023-081_POI_773600_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09889 | 133.26 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09894 | 133.29 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.099 | 133.51 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09901 | 133.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09901 | 139.3 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09911 | 133.33 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09922 | 133.61 | P42:345:OKGE:SB_BAER7318:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09924 | 133.29 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09931 | 133.2 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09936 | 133.56 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09948 | 133.57 | P42:345:OKGE:SB_SEOL7385:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09966 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09966 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0999 | 133.93 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 134.9 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 134.91 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 135.3 | P13:69-115:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 135.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10007 | 136.02 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10071 | 138.51 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10085 | 137.34 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10096 | 136.22 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10096 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10096 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10182 | 139.38 | Potential P4 Event - POI 515458_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10223 | 137.06 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10345 | 137.63 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10465 | 135.99 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10696 | 138.61 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10916 | 140.79 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11439 | 163.65 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11588 | 157.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11588 | 157.17 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11588 | 157.17 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.14874 | 188.65 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15538 | 161.82 | Potential P4 Event - POI 527656_9 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 161.31 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 161.31 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 164.87 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 164.87 | Potential P4 Event - POI 527656_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15634 | 163.21 | Potential P4 Event - POI 527656_13 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15634 | 163.21 | Potential P4 Event - POI 527656_14 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15745 | 163.83 | Potential P4 Event - POI 527656_0 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09851 | 134.6 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09874 | 134.9 | P23:345:WERE:JEC-345-16:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09874 | 134.92 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09875 | 134.93 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09875 | 142.83 | Potential P4 Event - POI 773600_1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09876 | 134.94 | P11:345:WERE:JECU3-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09876 | 142.91 | Potential P4 Event - POI 773600_7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09876 | 142.91 | Potential P4 Event - POI 773600_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09877 | 134.83 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09878 | 134.63 | 514787 DEWEY 4 138 515533 REDCLFT4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09878 | 134.63 | 514789 MENOTAP4 138 514790 IMO 4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09878 | 134.82 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09879 | 134.83 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0988 | 134.83 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0988 | 134.83 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0988 | 135.25 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09881 | 134.82 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.3 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.64 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.82 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.83 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.83 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.86 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.87 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.89 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.92 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.92 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.92 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.93 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.93 | P23:345:XEL:8H14 PRI | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.93 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.94 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.94 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.95 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.96 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.96 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.96 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.96 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.97 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.97 | P23:345:XEL:8N22 SHC | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.97 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.98 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.98 | P23:345:MEC:LOUISA 964 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.99 | P23:345:MEC:CBEC 905 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.99 | P23:345:MEC:LOUISA 954 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.01 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.02 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.02 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.02 | P23:500:EES-EAI:WH_BLF:B7942 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.03 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.03 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.04 | P11:26:EES-EAI:INDEP2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.04 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.04 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.04 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.04 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.05 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.05 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.05 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.06 | ASGI-2021-001_POI_766031_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.06 | ASGI-2023-001_POI_528252_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.06 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.06 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.07 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.1 | P11:21:EES:RVB:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.11 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.11 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.14 | P11:25:EES:WATERF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.14 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.14 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.21 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.23 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.27 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.34 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 137.63 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 137.79 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 137.99 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 138.62 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 138.62 | GEN-2023-201_POI_776000_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 139.4 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 139.4 | GEN-2023-236_POI_776700_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 142.7 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 142.7 | GEN-2023-081_POI_773600_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09883 | 134.97 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09897 | 135.31 | P42:345:OKGE:SB_BVTY7387:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.099 | 135.72 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09901 | 135.59 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09901 | 142.25 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09911 | 135.19 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09922 | 135.54 | P42:345:OKGE:SB_BAER7318:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09924 | 135.05 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09931 | 134.98 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09936 | 135.28 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09966 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09966 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0999 | 135.66 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 136.85 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 136.86 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 137.23 | P13:69-115:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 137.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10007 | 137.76 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10071 | 140.57 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10085 | 139.06 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10096 | 137.62 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10096 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10096 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10182 | 141.48 | Potential P4 Event - POI 515458_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10223 | 139.08 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10345 | 138.3 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10465 | 138.08 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10696 | 140.18 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10916 | 142.88 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11439 | 165.72 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11588 | 159.05 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11588 | 159.06 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11588 | 159.06 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.14874 | 190.26 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 165.89 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 165.89 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 169.93 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 169.93 | Potential P4 Event - POI 527656_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15634 | 167.9 | Potential P4 Event - POI 527656_13 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15634 | 167.9 | Potential P4 Event - POI 527656_14 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15684 | 166.55 | Potential P4 Event - POI 527656_10 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15745 | 167.97 | Potential P4 Event - POI 527656_0 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.12828 | 111.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13736 | 100.57 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13736 | 100.57 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.1377 | 101.14 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.17233 | 115.99 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.17629 | 106.67 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18655 | 105.86 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18655 | 106.45 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18655 | 106.45 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18655 | 106.45 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18681 | 107.23 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18681 | 107.23 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18705 | 106.66 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18717 | 107.87 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 100.95 | 524757 BETHEL_COL 3 115 524756 BETHEL_COL21 34.5 2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 101.91 | 774381 GEN-2023-120 115 774382 G23-120XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 101.91 | GEN-2023-120_POI_525192_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 103.92 | 524757 BETHEL_COL 3 115 524755 BETHEL_COL11 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 105.74 | GEN-2014-040_POI_524746_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07668 | 101.48 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07718 | 100.83 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07718 | 101.21 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07828 | 102.98 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07828 | 104.53 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07923 | 102.37 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0802 | 104.71 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08127 | 118.26 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08684 | 115.9 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09001 | 114.03 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09001 | 114.37 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09001 | 114.37 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09006 | 114.65 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09006 | 114.65 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09009 | 114.42 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09013 | 114.86 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0925 | 119.12 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.10331 | 125.72 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 101.37 | 524757 BETHEL_COL 3 115 524756 BETHEL_COL21 34.5 2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 101.99 | 774381 GEN-2023-120 115 774382 G23-120XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 101.99 | GEN-2023-120_POI_525192_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 103.73 | 524757 BETHEL_COL 3 115 524755 BETHEL_COL11 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 106.35 | GEN-2014-040_POI_524746_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07668 | 101.45 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07718 | 101.04 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07718 | 101.45 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07828 | 103.25 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07828 | 104.94 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07923 | 102.48 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0802 | 104.88 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08127 | 120.17 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08684 | 116.62 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09001 | 114.55 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09001 | 114.92 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09001 | 114.92 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09006 | 115.22 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09006 | 115.22 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09009 | 114.98 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09013 | 115.44 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0925 | 119.36 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.10331 | 126.07 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1119 | 139.31 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15186 | 135.64 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15186 | 135.64 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15189 | 135.15 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15193 | 135.16 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15196 | 135.07 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15197 | 135.48 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.02 | 562727 LESBIA 115 562728 SANJONTAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.07 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.14 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.15 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.17 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.38 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.38 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.44 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.47 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.47 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.49 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.52 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.52 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.52 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.52 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.55 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.55 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.57 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.59 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.62 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.62 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.7 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.7 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.7 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.7 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.72 | P11:26:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.72 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.72 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.73 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.73 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.73 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.75 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.75 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.76 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.77 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.78 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.83 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.95 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.95 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.95 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.95 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.95 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.98 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.98 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.02 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.02 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.02 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.24 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.24 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.47 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.47 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.47 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 137.36 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 139.3 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15199 | 135.15 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15201 | 135.16 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15201 | 135.39 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15202 | 135.15 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15202 | 135.15 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15202 | 135.15 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15202 | 135.44 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15202 | 135.45 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15203 | 135.02 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15203 | 135.49 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15203 | 135.56 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15203 | 135.56 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15209 | 135.63 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1521 | 135.61 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15212 | 135.65 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15212 | 135.73 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15213 | 135.62 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15218 | 136 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15222 | 135.63 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15224 | 135.96 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15224 | 135.96 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15251 | 137.34 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15251 | 137.43 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15251 | 137.43 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15257 | 137.04 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15257 | 137.04 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15259 | 137.06 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15259 | 137.16 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15265 | 137.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15266 | 136.61 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15301 | 137.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15311 | 137.41 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15311 | 137.41 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15314 | 138.33 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1533 | 137.58 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15331 | 137.59 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15334 | 137.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15394 | 141.34 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15398 | 141.38 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15406 | 141.62 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15406 | 141.62 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15464 | 141.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15579 | 142.78 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15579 | 142.94 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1581 | 139.39 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15832 | 138.87 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15887 | 139.19 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15956 | 147.71 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15956 | 148.81 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1633 | 143.07 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16562 | 152.28 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16562 | 159.07 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16562 | 161.78 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16562 | 163.27 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16841 | 149.61 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1717 | 163.49 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 162.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 164.73 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 164.73 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20168 | 165.04 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20168 | 165.04 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20192 | 165.64 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.202 | 164.89 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21015 | 109.73 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21015 | 110.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10483 | 113.29 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17935 | 109.05 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17935 | 109.05 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17954 | 108.48 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17954 | 108.48 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17957 | 108.48 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17957 | 108.65 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17957 | 108.87 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.39 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.46 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.48 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.64 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.64 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.67 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.67 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.79 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.82 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.82 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.87 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.89 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.9 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.9 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.92 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.94 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.94 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.99 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.99 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.03 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.04 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.14 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.15 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.15 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.16 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.17 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.17 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.17 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.18 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.18 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.18 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.22 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.22 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.23 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.24 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.26 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.3 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.37 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.4 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.49 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.49 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.49 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.49 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.49 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.53 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.53 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.53 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.58 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.58 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.59 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.69 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.69 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.69 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.75 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.75 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.78 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.66 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 111.04 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 111.24 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 113.28 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17964 | 108.45 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17964 | 108.45 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17964 | 108.45 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 108.69 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 108.76 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17966 | 108.77 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17967 | 108.28 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17967 | 108.82 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17968 | 108.9 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17968 | 108.9 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17979 | 108.98 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1798 | 108.95 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17985 | 108.99 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17993 | 109.13 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17993 | 109.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17996 | 109.44 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18003 | 108.99 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18006 | 109.39 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18006 | 109.39 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18059 | 111.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18059 | 111.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1806 | 111.09 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1807 | 110.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1807 | 110.68 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18074 | 110.71 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18074 | 110.82 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1808 | 110.1 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18088 | 110.77 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18165 | 112.1 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18184 | 111.03 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18184 | 111.04 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18201 | 111.42 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18266 | 113.28 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18295 | 112.35 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18295 | 112.35 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18329 | 115.8 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18335 | 115.86 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18351 | 116.15 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18351 | 116.15 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18472 | 116.25 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18515 | 117.38 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1864 | 117.14 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1864 | 117.29 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19004 | 118.97 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19225 | 121.61 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19225 | 122.52 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20042 | 124.23 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20447 | 138.42 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 128.24 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 131.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 135.41 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 135.88 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 138.79 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 139.6 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 139.63 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 140.37 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 119.52 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 119.53 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29756 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15973 | 100.92 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15979 | 100.97 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15992 | 101.22 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15992 | 101.22 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16098 | 101.31 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16135 | 102.3 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16244 | 102.08 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16244 | 102.22 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16562 | 103.69 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16754 | 105.99 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16754 | 106.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17466 | 108.27 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17818 | 120.63 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 111.76 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 115 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 118.01 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 118.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 120.96 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 121.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 121.68 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 122.33 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18849 | 104.17 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18849 | 104.17 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28714 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11603 | 102.88 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22324 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22435 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22435 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22435 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2245 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2245 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22456 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22456 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22469 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22474 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22595 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22628 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22629 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22646 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22651 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22685 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22685 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22783 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22816 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22825 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22841 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22847 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22848 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2301 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23078 | 107.18 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23083 | 106.47 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23083 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2319 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23285 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24205 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25113 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25198 | 104.54 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2663 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38265 | 154.86 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41996 | 188.13 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4214 | 187.42 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 183.57 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 183.59 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 195.61 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22208 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24432 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38232 | 155.38 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41955 | 188.56 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42097 | 187.81 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 184.02 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 184.11 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 196.06 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10483 | 114.16 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17935 | 109.42 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17935 | 109.42 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17954 | 108.86 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17954 | 108.86 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17957 | 108.86 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17957 | 109.03 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17957 | 109.24 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.77 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.83 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.84 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.86 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.02 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.02 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.07 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.07 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.17 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.19 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.19 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.25 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.27 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.27 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.27 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.29 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.31 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.31 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.36 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.36 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.4 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.41 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.51 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.52 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.52 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.53 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.54 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.54 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.54 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.54 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.55 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.55 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.59 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.59 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.6 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.6 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.62 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.66 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.73 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.77 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.85 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.85 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.85 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.85 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.85 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.89 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.89 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.9 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.95 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.95 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.95 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.17 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.17 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.17 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.25 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.25 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 111.11 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 111.53 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 111.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 114.16 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17964 | 108.84 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17964 | 108.84 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17964 | 108.84 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 109.07 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 109.14 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17966 | 109.14 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17967 | 108.67 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17967 | 109.19 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17968 | 109.27 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17968 | 109.27 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17979 | 109.35 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1798 | 109.33 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17985 | 109.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17993 | 109.5 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17993 | 109.62 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17996 | 109.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18003 | 109.36 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18006 | 109.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18006 | 109.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18059 | 111.45 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18059 | 111.45 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1806 | 111.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1807 | 111 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1807 | 111 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18074 | 111.03 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18074 | 111.14 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1808 | 110.42 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18088 | 111.06 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18165 | 112.34 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18184 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18184 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18201 | 111.7 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18266 | 113.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18295 | 112.76 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18295 | 112.76 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18329 | 116 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18335 | 116.05 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18351 | 116.33 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18351 | 116.33 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18472 | 116.57 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18526 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1864 | 117.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1864 | 117.33 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19004 | 119.68 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19225 | 121.98 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19225 | 122.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20042 | 124.63 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20447 | 141.25 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 130.11 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 134.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 137.98 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 138.46 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 141.54 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 142.35 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 142.4 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 143.16 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 118.53 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 120.63 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 120.63 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29756 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15973 | 101.1 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15979 | 101.14 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15992 | 101.39 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15992 | 101.39 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16098 | 101.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16244 | 102.12 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16244 | 102.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16562 | 104.3 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16754 | 106.31 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16754 | 107.11 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17466 | 108.62 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17818 | 123.1 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 113.4 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 117.19 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 120.26 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 120.67 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 123.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 124.06 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 124.1 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 124.76 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18849 | 103.3 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18849 | 105.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18849 | 105.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28714 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10288 | 119.45 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 106.79 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 109.48 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 114.6 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 115.27 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 119.86 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 120.54 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 120.55 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 121.12 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10337 | 111.33 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-005 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.11581 | 112.72 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09698 | 108.49 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09698 | 108.49 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0679 | 104.05 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06874 | 105.19 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06882 | 106.48 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06882 | 106.5 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06908 | 106.75 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06913 | 103.66 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06915 | 104.31 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06915 | 106.39 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06918 | 104.64 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06918 | 105.34 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06932 | 103.96 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06936 | 103.86 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06949 | 103.86 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06951 | 104.29 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06951 | 104.3 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06953 | 104.25 | P11:18:HAST::EGYCTR2G WEC2:LOSS OF WEC 2 GEN:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06953 | 104.25 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06956 | 103.62 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06961 | 103.95 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06965 | 104.21 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06969 | 103.7 | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 103.19 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 103.19 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 103.22 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 103.36 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 103.65 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 103.87 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 103.87 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 103.87 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 103.87 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 103.87 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 103.94 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 103.95 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 104.01 | P13:NBEC#1 GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 104.1 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 104.18 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 104.28 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 104.31 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 104.65 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 104.66 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 104.71 | 531504 CIMWD2 7 345 3WXFMR CIMRNWND2 MPT 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 104.71 | GEN-2010-009_POI_531501_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 104.74 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 104.75 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 104.75 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 104.75 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 104.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 104.87 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 104.87 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 105.04 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 105.14 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 105.15 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 105.37 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 105.37 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 105.49 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 105.49 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 105.51 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 105.53 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 105.64 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 105.65 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 105.72 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 105.74 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 105.88 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 105.91 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06973 | 111.31 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06974 | 103.2 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06974 | 103.33 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06974 | 105.63 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06975 | 103.48 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06978 | 103.3 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06978 | 103.41 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06978 | 103.46 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06978 | 103.48 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06979 | 103.26 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06979 | 103.92 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06979 | 103.92 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06979 | 103.97 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0698 | 103.43 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0698 | 103.62 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06981 | 104.56 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06985 | 103.51 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06986 | 103.92 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06986 | 104.02 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06988 | 103.93 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06988 | 104.19 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06989 | 104.29 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0699 | 103.85 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06991 | 104.21 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06991 | 104.21 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06991 | 104.28 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06994 | 104.04 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06995 | 103.53 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06996 | 103.72 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06997 | 103.77 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07004 | 103.57 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07004 | 105.27 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07005 | 103.96 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07007 | 104.43 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07007 | 105.48 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07025 | 104.04 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0703 | 103.64 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07038 | 104.27 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07044 | 104.71 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07044 | 104.71 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07047 | 104.64 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07049 | 104.7 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07049 | 104.71 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07051 | 104.3 | P12:345:WERE:VIOL-WICH-345:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07079 | 104.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07082 | 111.68 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07102 | 106.65 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07102 | 106.7 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07118 | 104.54 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07132 | 106 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07155 | 104.72 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07155 | 104.73 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0718 | 104.85 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0718 | 104.85 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07192 | 104.84 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07197 | 106.71 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07245 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07245 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07245 | 105.45 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07248 | 106.03 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07256 | 105.86 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07264 | 108.97 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07273 | 109.15 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07276 | 109.43 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07307 | 107.32 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07307 | 107.46 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07307 | 107.57 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07307 | 109.51 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07721 | 111.96 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07811 | 120.22 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07811 | 120.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07811 | 120.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07811 | 120.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07811 | 120.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07886 | 124.48 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07886 | 124.48 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07886 | 124.48 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09215 | 126.32 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09215 | 126.32 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09215 | 126.32 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09437 | 135.92 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09437 | 135.92 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08072 | 106.45 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08072 | 106.46 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08072 | 106.46 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08072 | 106.46 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08072 | 106.46 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08147 | 110.51 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08147 | 110.51 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08147 | 110.51 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09475 | 112.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09475 | 112.81 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09475 | 112.81 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09698 | 122.53 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09698 | 122.53 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05009 | 133.56 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05032 | 133.57 | P42:345:OKGE:SB_SEOL7385:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05034 | 137.34 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05044 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05044 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05059 | 138.51 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05162 | 137.06 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05217 | 136.22 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05217 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05217 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05311 | 139.3 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05314 | 137.63 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05332 | 136.02 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05386 | 133.93 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05612 | 163.65 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0576 | 157.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0576 | 157.17 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0576 | 157.17 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06028 | 139.38 | Potential P4 Event - POI 515458_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06555 | 138.61 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06616 | 161.82 | Potential P4 Event - POI 527656_9 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06631 | 161.31 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06631 | 161.31 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06631 | 164.87 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06631 | 164.87 | Potential P4 Event - POI 527656_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06696 | 163.21 | Potential P4 Event - POI 527656_13 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06696 | 163.21 | Potential P4 Event - POI 527656_14 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0677 | 163.83 | Potential P4 Event - POI 527656_0 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06995 | 140.79 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07617 | 188.65 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05009 | 135.28 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05034 | 139.06 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05044 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05044 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05059 | 140.57 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05162 | 139.08 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05217 | 137.62 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05217 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05217 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05311 | 142.25 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05314 | 138.3 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05332 | 137.76 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05386 | 135.66 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05612 | 165.72 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0576 | 159.05 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0576 | 159.06 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0576 | 159.06 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06028 | 141.48 | Potential P4 Event - POI 515458_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06555 | 140.18 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06631 | 165.89 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06631 | 165.89 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06631 | 169.93 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06631 | 169.93 | Potential P4 Event - POI 527656_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06696 | 167.9 | Potential P4 Event - POI 527656_13 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06696 | 167.9 | Potential P4 Event - POI 527656_14 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06705 | 166.55 | Potential P4 Event - POI 527656_10 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0677 | 167.97 | Potential P4 Event - POI 527656_0 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06995 | 142.88 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07617 | 190.26 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.06299 | 109.73 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.06299 | 110.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2835 | 113.29 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35171 | 138.42 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35336 | 128.24 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35336 | 131.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35336 | 135.41 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35336 | 135.88 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35336 | 138.79 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35336 | 139.6 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35336 | 139.63 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35336 | 140.37 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35802 | 109.05 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35802 | 109.05 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3582 | 108.48 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3582 | 108.48 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35823 | 108.48 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35823 | 108.65 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35823 | 108.87 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.39 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.46 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.48 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.64 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.64 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.67 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.67 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.79 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.82 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.82 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.87 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.89 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.9 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.9 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.92 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.94 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.94 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.99 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.03 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.04 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.14 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.15 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.15 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.16 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.17 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.17 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.17 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.18 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.18 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.18 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.22 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.22 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.23 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.24 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.26 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.3 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.37 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.4 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.49 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.49 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.49 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.49 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.49 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.53 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.53 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.53 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.58 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.58 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.59 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.69 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.69 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.69 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.75 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.75 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.78 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 110.66 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 110.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 111.04 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 111.24 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 113.28 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35825 | 108.99 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3583 | 108.45 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3583 | 108.45 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3583 | 108.45 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3583 | 108.69 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35831 | 108.82 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35832 | 108.76 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35832 | 108.77 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35833 | 108.9 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35833 | 108.9 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35834 | 108.28 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35842 | 108.95 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35843 | 108.98 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35844 | 109.13 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35844 | 109.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3585 | 108.99 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35859 | 109.44 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35865 | 108.99 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35865 | 109.39 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35865 | 109.39 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35895 | 110.1 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35896 | 111.09 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35906 | 110.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35906 | 110.68 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35913 | 111.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35913 | 111.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35914 | 110.77 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35915 | 111.03 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35916 | 111.04 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35927 | 110.71 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35927 | 110.82 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35959 | 113.28 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35988 | 112.35 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35988 | 112.35 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36015 | 112.1 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36044 | 111.42 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36083 | 116.25 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36123 | 115.8 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36131 | 115.86 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36146 | 116.15 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36146 | 116.15 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36216 | 117.14 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36216 | 117.29 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36281 | 117.38 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36345 | 121.61 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36345 | 122.52 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36347 | 118.97 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36925 | 119.52 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36925 | 119.53 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36946 | 124.23 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.59362 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30651 | 120.63 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30794 | 111.76 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30794 | 115 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30794 | 118.01 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30794 | 118.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30794 | 120.96 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30794 | 121.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30794 | 121.68 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30794 | 122.33 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31445 | 101.31 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3148 | 100.92 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31487 | 100.97 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.315 | 101.22 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.315 | 101.22 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31561 | 102.08 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31561 | 102.22 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31618 | 102.3 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31674 | 105.99 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31674 | 106.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31675 | 103.69 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.32179 | 104.17 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.32179 | 104.17 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.32197 | 108.27 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.57283 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23375 | 102.88 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34063 | 100.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34063 | 100.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34063 | 100.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34063 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34063 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34063 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34063 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34063 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34063 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34063 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34063 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34063 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34063 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34063 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34164 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34165 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34178 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34178 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34189 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34189 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.3419 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34199 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34199 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34209 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34209 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.3422 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34254 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34254 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34341 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34383 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34425 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34469 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34486 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34497 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34512 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34513 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34517 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34518 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34634 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34707 | 107.18 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34712 | 106.47 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34712 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34716 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.3485 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34909 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34976 | 104.54 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.36396 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.63295 | 188.13 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.64289 | 187.42 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.64958 | 183.57 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.64958 | 183.59 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.64958 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.64958 | 195.61 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.65822 | 154.86 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31974 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.33393 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.63233 | 188.56 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.64224 | 187.81 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.64892 | 184.02 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.64892 | 184.11 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.64892 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.64892 | 196.06 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.65765 | 155.38 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2835 | 114.16 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35171 | 141.25 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35336 | 130.11 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35336 | 134.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35336 | 137.98 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35336 | 138.46 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35336 | 141.54 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35336 | 142.35 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35336 | 142.4 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35336 | 143.16 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35802 | 109.42 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35802 | 109.42 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3582 | 108.86 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3582 | 108.86 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35823 | 108.86 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35823 | 109.03 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35823 | 109.24 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.77 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.83 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.84 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 108.86 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.02 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.02 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.07 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.07 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.17 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.19 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.19 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.25 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.27 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.27 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.27 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.29 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.31 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.31 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.36 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.4 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.41 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.51 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.52 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.52 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.53 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.54 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.54 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.54 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.54 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.55 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.55 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.59 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.59 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.6 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.6 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.62 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.66 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.73 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.77 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.85 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.85 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.85 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.85 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.85 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.89 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.89 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.9 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.95 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.95 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 109.95 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 110.17 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 110.17 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 110.17 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 110.25 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 110.25 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 110.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 111.11 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 111.53 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 111.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35824 | 114.16 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35825 | 109.36 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3583 | 108.84 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3583 | 108.84 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3583 | 108.84 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3583 | 109.07 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35831 | 109.19 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35832 | 109.14 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35832 | 109.14 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35833 | 109.27 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35833 | 109.27 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35834 | 108.67 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35842 | 109.33 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35843 | 109.35 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35844 | 109.5 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35844 | 109.62 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3585 | 109.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35859 | 109.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35861 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35865 | 109.36 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35865 | 109.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35865 | 109.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35895 | 110.42 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35896 | 111.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35906 | 111 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35906 | 111 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35913 | 111.45 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35913 | 111.45 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35914 | 111.06 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35915 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35916 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35927 | 111.03 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35927 | 111.14 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35959 | 113.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35988 | 112.76 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35988 | 112.76 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36015 | 112.34 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36044 | 111.7 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36083 | 116.57 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36123 | 116 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36131 | 116.05 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36146 | 116.33 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36146 | 116.33 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36216 | 117.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36216 | 117.33 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36345 | 121.98 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36345 | 122.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36347 | 119.68 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36925 | 118.53 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36925 | 120.63 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36925 | 120.63 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36946 | 124.63 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.59362 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30651 | 123.1 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30794 | 113.4 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30794 | 117.19 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30794 | 120.26 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30794 | 120.67 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30794 | 123.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30794 | 124.06 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30794 | 124.1 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30794 | 124.76 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31445 | 101.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3148 | 101.1 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31487 | 101.14 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.315 | 101.39 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.315 | 101.39 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31561 | 102.12 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31561 | 102.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31674 | 106.31 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31674 | 107.11 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31675 | 104.3 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.32179 | 103.3 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.32179 | 105.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.32179 | 105.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.32197 | 108.62 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.57283 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05056 | 139.38 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05056 | 139.57 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05056 | 139.79 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05056 | 139.79 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05056 | 133.85 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05056 | 134.04 | POI 515800_22 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05056 | 134.04 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05056 | 134.12 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05056 | 134.12 | Potential P4 Event - POI 560078_2 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05056 | 137.92 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05056 | 138.2 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05056 | 138.5 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05056 | 138.5 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | 353 | 353 | 0.11396 | 108.18 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing STLN-DEMARCO6 to G23-101-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.15565 | 108.49 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.15565 | 108.49 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12413 | 105.19 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1242 | 106.48 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12421 | 106.5 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12437 | 103.66 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12447 | 106.75 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12453 | 106.39 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12454 | 104.31 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1247 | 103.96 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12475 | 103.86 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12488 | 103.86 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1249 | 104.29 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1249 | 104.3 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12492 | 104.25 | P11:18:HAST::EGYCTR2G WEC2:LOSS OF WEC 2 GEN:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12492 | 104.25 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12495 | 103.62 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12499 | 103.95 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12503 | 104.21 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12508 | 103.7 | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 103.19 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 103.19 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 103.2 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 103.22 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 103.33 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 103.36 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 103.65 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 103.87 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 103.87 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 103.87 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 103.87 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 103.87 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 103.94 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 103.95 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 104.01 | P13:NBEC#1 GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 104.1 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 104.18 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 104.28 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 104.31 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 104.65 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 104.66 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 104.71 | 531504 CIMWD2 7 345 3WXFMR CIMRNWND2 MPT 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 104.71 | GEN-2010-009_POI_531501_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 104.74 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 104.75 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 104.75 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 104.75 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 104.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 104.87 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 104.87 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 105.04 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 105.14 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 105.15 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 105.37 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 105.37 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 105.49 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 105.49 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 105.51 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 105.53 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 105.63 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 105.64 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 105.65 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 105.72 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 105.74 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 105.88 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 105.91 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12512 | 111.31 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12513 | 103.48 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12515 | 103.3 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12515 | 103.46 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12515 | 103.48 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12515 | 103.62 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12515 | 103.92 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12515 | 103.92 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12515 | 103.97 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12516 | 103.26 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12516 | 103.41 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12517 | 104.56 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12519 | 103.43 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1252 | 103.92 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1252 | 104.02 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12521 | 103.51 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12521 | 104.19 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12522 | 104.29 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12523 | 103.93 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12523 | 104.28 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12526 | 103.53 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12526 | 103.72 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12526 | 103.77 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12528 | 103.85 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12528 | 104.21 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12528 | 104.21 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12529 | 103.96 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12532 | 104.04 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12532 | 105.27 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12533 | 105.48 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12535 | 104.43 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12538 | 103.57 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12551 | 104.3 | P12:345:WERE:VIOL-WICH-345:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12552 | 104.27 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12555 | 104.71 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12555 | 104.71 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12557 | 104.64 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12559 | 103.64 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12592 | 104.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12594 | 104.05 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12608 | 106 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12609 | 104.54 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12639 | 104.7 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12639 | 104.71 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1264 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1264 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1264 | 105.45 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12645 | 106.71 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12663 | 104.72 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12663 | 104.73 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12665 | 104.84 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12666 | 104.64 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12666 | 105.34 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12669 | 104.85 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12669 | 104.85 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12677 | 111.68 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12714 | 104.04 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12739 | 106.03 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12747 | 105.86 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.13036 | 109.43 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.13088 | 107.32 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.13088 | 107.46 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.13088 | 107.57 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.13088 | 109.51 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.13134 | 108.97 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.13159 | 106.65 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.13159 | 106.7 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1329 | 109.15 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.13378 | 111.96 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.13961 | 120.22 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.13961 | 120.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.13961 | 120.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.13961 | 120.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.13961 | 120.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.15167 | 126.32 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.15167 | 126.32 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.15167 | 126.32 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.15304 | 135.92 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.15304 | 135.92 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.17089 | 124.48 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.17089 | 124.48 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.17089 | 124.48 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.14222 | 106.45 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.14222 | 106.46 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.14222 | 106.46 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.14222 | 106.46 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.14222 | 106.46 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.15428 | 112.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.15428 | 112.81 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.15428 | 112.81 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.15565 | 122.53 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.15565 | 122.53 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1735 | 110.51 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1735 | 110.51 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1735 | 110.51 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.29261 | 188.65 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3002 | 139.38 | Potential P4 Event - POI 515458_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3013 | 139.3 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30172 | 137.63 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30216 | 133.93 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30233 | 138.51 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30274 | 163.83 | Potential P4 Event - POI 527656_0 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30288 | 136.02 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30326 | 163.21 | Potential P4 Event - POI 527656_13 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30326 | 163.21 | Potential P4 Event - POI 527656_14 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30347 | 161.82 | Potential P4 Event - POI 527656_9 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30362 | 161.31 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30362 | 161.31 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30362 | 164.87 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30362 | 164.87 | Potential P4 Event - POI 527656_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30387 | 138.87 | Potential P4 Event - POI 773600_4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30389 | 138.88 | Potential P4 Event - POI 773600_7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30389 | 138.88 | Potential P4 Event - POI 773600_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30393 | 132.94 | P23:345:WERE:JEC-345-16:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30394 | 133 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30395 | 132.62 | 514796 IODINE-4 138 515376 WWRDEHV4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30395 | 132.62 | 514796 IODINE-4 138 515533 REDCLFT4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30395 | 133.01 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30397 | 132.82 | 532792 FR2EAST7 345 588364 G16-153-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30397 | 132.87 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30397 | 132.92 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30399 | 132.81 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30399 | 132.83 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30399 | 132.85 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30399 | 132.88 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30399 | 132.88 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.304 | 133.45 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.45 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.59 | 659387 KUMMERDG-BE3 345 659390 PATENTGT-BE3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.61 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.81 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.81 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.84 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.84 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.84 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.86 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.9 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.9 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.91 | P12:069:GLHP:COLE-TURPIN-BEARD-ADAMS-JEFFERSON:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.93 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.94 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.95 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.96 | ASGI-2023-001_POI_528252_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.96 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.96 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.98 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.99 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.99 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.99 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 132.99 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133 | P12:EHV:EES::8ISES%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133 | P23:345:XEL:8H14 PRI | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.01 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.01 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.04 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.04 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.05 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.05 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.05 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.06 | P11:21:EES:RVB:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.06 | P11:HV:EES::1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.06 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.06 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.06 | P23:345:MEC:LOUISA 964 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.07 | P23:345:XEL:8N22 SHC | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.09 | P11:25:EES:WATERF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.09 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.09 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.09 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.09 | P23:345:MEC:CBEC 908 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.1 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.11 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.11 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.11 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.11 | P23:345:MEC:CBEC 905 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.15 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.18 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.19 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.19 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.21 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.28 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.3 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 133.47 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.76 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.88 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.24 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.42 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.43 | GEN-2023-201_POI_776000_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.91 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.91 | GEN-2023-236_POI_776700_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 138.67 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 138.67 | GEN-2023-081_POI_773600_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30402 | 132.96 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30402 | 133.04 | P23:500:EES-EAI:INDEP2:B6126 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30418 | 133.26 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30419 | 133.29 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30428 | 133.57 | P42:345:OKGE:SB_SEOL7385:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3043 | 133.56 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30434 | 133.29 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30435 | 133.51 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30436 | 133.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30441 | 133.2 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30454 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30454 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30474 | 133.33 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30491 | 135.99 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30503 | 133.61 | P42:345:OKGE:SB_BAER7318:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30536 | 136.22 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30536 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30536 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30557 | 137.06 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3058 | 134.9 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3058 | 134.91 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3058 | 135.3 | P13:69-115:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3058 | 135.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30764 | 138.61 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30863 | 140.79 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30915 | 137.34 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.33465 | 163.65 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.33613 | 157.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.33613 | 157.17 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.33613 | 157.17 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.29261 | 190.26 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3002 | 141.48 | Potential P4 Event - POI 515458_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3013 | 142.25 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30172 | 138.3 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30216 | 135.66 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30233 | 140.57 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30274 | 167.97 | Potential P4 Event - POI 527656_0 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30288 | 137.76 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30326 | 167.9 | Potential P4 Event - POI 527656_13 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30326 | 167.9 | Potential P4 Event - POI 527656_14 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30327 | 166.55 | Potential P4 Event - POI 527656_10 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30357 | 134.6 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30362 | 165.89 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30362 | 165.89 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30362 | 169.93 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30362 | 169.93 | Potential P4 Event - POI 527656_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30387 | 142.83 | Potential P4 Event - POI 773600_1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30389 | 142.91 | Potential P4 Event - POI 773600_7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30389 | 142.91 | Potential P4 Event - POI 773600_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30393 | 134.9 | P23:345:WERE:JEC-345-16:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30394 | 134.92 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30395 | 134.63 | 514787 DEWEY 4 138 515533 REDCLFT4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30395 | 134.93 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30395 | 134.94 | P11:345:WERE:JECU3-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30397 | 134.63 | 514789 MENOTAP4 138 514790 IMO 4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30397 | 134.82 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30397 | 134.83 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30399 | 134.83 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30399 | 134.83 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30399 | 134.83 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.304 | 135.25 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.3 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.64 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.82 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.82 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.83 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.83 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.86 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.87 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.89 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.92 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.92 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.92 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.93 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.93 | P23:345:XEL:8H14 PRI | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.93 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.94 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.94 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.95 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.96 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.96 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.96 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.96 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.97 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.97 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.97 | P23:345:XEL:8N22 SHC | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.97 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.98 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.98 | P23:345:MEC:LOUISA 964 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.99 | P23:345:MEC:CBEC 905 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 134.99 | P23:345:MEC:LOUISA 954 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.01 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.02 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.02 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.02 | P23:500:EES-EAI:WH_BLF:B7942 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.03 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.03 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.04 | P11:26:EES-EAI:INDEP2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.04 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.04 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.04 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.04 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.05 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.05 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.05 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.06 | ASGI-2021-001_POI_766031_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.06 | ASGI-2023-001_POI_528252_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.06 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.06 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.07 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.1 | P11:21:EES:RVB:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.11 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.11 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.14 | P11:25:EES:WATERF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.14 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.14 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.21 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.23 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.27 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 135.34 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 137.63 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 137.79 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 137.99 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 138.62 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 138.62 | GEN-2023-201_POI_776000_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 139.4 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 139.4 | GEN-2023-236_POI_776700_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 142.7 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30401 | 142.7 | GEN-2023-081_POI_773600_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3043 | 135.28 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30434 | 135.05 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30435 | 135.72 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30436 | 135.59 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30441 | 134.98 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30441 | 135.31 | P42:345:OKGE:SB_BVTY7387:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30454 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30454 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30474 | 135.19 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2